## Connection Config
Connection Type | Device Brand | Device Name | Device Type | IP | Port | Timeout | Interval | Destination | Destination Location
TCP | Hithium | BMU_2 | bmu | 192.168.100.103 | 6003 | 3000 | 1000 | filesystem | data

## Modbus Address
address type | unit id | group | code name | display name | address name | function code | address | fix value | data type | bit length | signed type | endianness | scale | decimal places | offset | enable bit configuration | bit configuration | enable parse configuration | parse configuration | is warning variable | warning level | start address | data count | is heartbeat address | heartbeat interval
individual | 1 |  | UNDER_VOLT_SLIGHT | 總電壓欠壓_輕微 | system_undervoltage_slight_alarm | 2 | 1 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 |  | UNDER_VOLT_MEDIUM | 總電壓欠壓_中度 | system_undervoltage_medium_alarm | 2 | 2 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 2 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 |  | UNDER_VOLT_SERIOUS | 總電壓欠壓_嚴重 | system_voltage_undervoltage_serious_alarm | 2 | 3 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 |  | OVER_VOLT_SLIGHT | 總電壓過壓_輕微 | system_overvoltage_slight_alarm | 2 | 4 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 |  | OVER_VOLT_MEDIUM | 總電壓過壓_中度 | system_overvoltage_medium_alarm | 2 | 5 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 |  | OVER_VOLT_SERIOUS | 總電壓過壓_嚴重 | system_overvoltage_serious_alarm | 2 | 6 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 |  | OVER_CURRENT_SLIGHT | 過流_輕微 | system_overcurrent_slight_alarm | 2 | 7 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 |  | OVER_CURRENT_MEDIUM | 過流_中度 | system_overcurrent_medium_alarm | 2 | 8 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 |  | OVER_CURRENT_SERIOUS | 過流_嚴重 | system_overcurrent_serious_alarm | 2 | 9 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 |  | LOW_INSULATION_RESISTANCE_SLIGHT | 低絕緣電阻_輕微 | system_low_insulation_resistance_slight_alarm | 2 | 10 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 |  | LOW_INSULATION_RESISTANCE_MEDIUM | 低絕緣電阻_中度 | system_low_insulation_resistance_medium_alarm | 2 | 11 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 |  | LOW_INSULATION_RESISTANCE_SERIOUS | 低絕緣電阻_嚴重 | system_low_insulation_resistance_serious_alarm | 2 | 12 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 |  | LOW_TEMP_SLIGHT | 模組低溫_輕微 | system_module_low_temperature_slight_alarm | 2 | 13 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 |  | LOW_TEMP_MEDIUM | 模組低溫_中度 | system_module_low_temperature_medium_alarm | 2 | 14 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 |  | LOW_TEMP_SERIOUS | 模組低溫_嚴重 | system_module_low_temperature_serious_alarm | 2 | 15 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 |  | OVER_TEMP_SLIGHT | 模組高溫_輕微 | system_module_over_temperature_slight_alarm | 2 | 16 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 |  | OVER_TEMP_MEDIUM | 模組高溫_中度 | system_module_over_temperature_medium_alarm | 2 | 17 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 |  | OVER_TEMP_SERIOUS | 模組高溫_嚴重 | system_module_over_temperature_serious_alarm | 2 | 18 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 |  | CELL_OVER_VOLT_SLIGHT | 電芯過壓_輕微 | system_cell_over_voltage_slight_alarm | 2 | 19 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 |  | CELL_OVER_VOLT_MEDIUM | 電芯過壓_中度 | system_cell_over_voltage_medium_alarm | 2 | 20 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 |  | CELL_OVER_VOLT_SERIOUS | 電芯過壓_嚴重 | system_cell_over_voltage_serious_alarm | 2 | 21 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 |  | CELL_LOW_VOLT_SLIGHT | 電芯低壓_輕微 | system_cell_low_voltage_slight_alarm | 2 | 22 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 |  | CELL_LOW_VOLT_MEDIUM | 電芯低壓_中度 | system_cell_low_voltage_medium_alarm | 2 | 23 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 |  | CELL_LOW_VOLT_SERIOUS | 電芯低壓_嚴重 | system_cell_low_voltage_serious_alarm | 2 | 24 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 |  | CELL_DIFF_VOLT_SLIGHT | 電芯電壓差_輕微 | system_cell_differential_voltage_slight_alarm | 2 | 25 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 |  | CELL_DIFF_VOLT_MEDIUM | 電芯電壓差_中度 | system_cell_differential_voltage_medium_alarm | 2 | 26 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 |  | CELL_DIFF_VOLT_SERIOUS | 電芯電壓差_嚴重 | system_cell_differential_voltage_serious_alarm | 2 | 27 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 |  | CELL_LOW_TEMP_SLIGHT | 電芯低溫_輕微 | system_cell_low_temperature_slight_alarm | 2 | 28 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 |  | CELL_LOW_TEMP_MEDIUM | 電芯低溫_中度 | system_cell_low_temperature_medium_alarm | 2 | 29 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 |  | CELL_LOW_TEMP_SERIOUS | 電芯低溫_嚴重 | system_cell_low_temperature_serious_alarm | 2 | 30 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 |  | CELL_OVER_TEMP_SLIGHT | 電芯高溫_輕微 | system_cell_over_temperature_slight_alarm | 2 | 31 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 |  | CELL_OVER_TEMP_MEDIUM | 電芯高溫_中度 | system_cell_over_temperature_medium_alarm | 2 | 32 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 |  | CELL_OVER_TEMP_SERIOUS | 電芯高溫_嚴重 | system_cell_over_temperature_serious_alarm | 2 | 33 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 |  | CELL_DIFF_TEMP_SLIGHT | 電芯溫差_輕微 | system_cell_differential_temperature_slight_alarm | 2 | 34 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 |  | CELL_DIFF_TEMP_MEDIUM | 電芯溫差_中度 | system_cell_differential_temperature_medium_alarm | 2 | 35 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 |  | CELL_DIFF_TEMP_SERIOUS | 電芯溫差_嚴重 | system_cell_differential_temperature_serious_alarm | 2 | 36 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 |  | CELL_SOC_LOW_SLIGHT | 電芯SOC過低_輕微 | system_cell_soc_low_slight_alarm | 2 | 37 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 |  | CELL_SOC_LOW_MEDIUM | 電芯SOC過低_中度 | system_cell_soc_low_medium_alarm | 2 | 38 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 |  | CELL_SOC_LOW_SERIOUS | 電芯SOC過低_嚴重 | system_cell_soc_low_serious_alarm | 2 | 39 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 |  | CELL_SOC_HIGH_SLIGHT | 電芯SOC過高_輕微 | system_cell_soc_high_slight_alarm | 2 | 40 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 |  | CELL_SOC_HIGH_MEDIUM | 電芯SOC過高_中度 | system_cell_soc_high_medium_alarm | 2 | 41 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 |  | CELL_SOC_HIGH_SERIOUS | 電芯SOC過高_嚴重 | system_cell_soc_high_serious_alarm | 2 | 42 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 |  | CELL_SOH_LOW_SLIGHT | 電芯SOH過低_輕微 | system_cell_soh_low_slight_alarm | 2 | 43 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 |  | CELL_SOH_LOW_MEDIUM | 電芯SOH過低_中度 | system_cell_soh_low_medium_alarm | 2 | 44 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 |  | CELL_SOH_LOW_SERIOUS | 電芯SOH過低_嚴重 | system_cell_soh_low_serious_alarm | 2 | 45 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 |  | CELL_SOH_HIGH_SLIGHT | 電芯SOH過高_輕微 | system_cell_soh_high_slight_alarm | 2 | 46 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 |  | CELL_SOH_HIGH_MEDIUM | 電芯SOH過高_中度 | system_cell_soh_high_medium_alarm | 2 | 47 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 |  | CELL_SOH_HIGH_SERIOUS | 電芯SOH過高_嚴重 | system_cell_soh_high_serious_alarm | 2 | 48 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 |  | ESBCM_LOST_COMM | ESBCM失去通信 | system_each_cbmu_lost_communication | 2 | 49 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 |  | ESBMM_LOST_COMM | ESBMM失去通信 | system_each_measurement_board_lost_communication | 2 | 50 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 |  | ABN_VOLT | Rack壓差異常(20V) | system_abnormal_voltage_of_each_rack | 2 | 51 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 |  | ABN_DIS_CON | 接觸器異常斷開 | system_abnormal_disconnection_of_contactor | 2 | 52 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 |  | ABN_CLOSE_CON | 接觸器異常關閉 | system_abnormal_closing_of_contactor | 2 | 53 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 |  | CHARGE_PROHIBIT | 禁充 | system_charging_prohibited | 2 | 54 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 |  | DISCHARGE_PROHIBIT | 禁放 | system_discharging_prohibited | 2 | 55 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 |  | BMS_ALARM | 系統告警 | system_bms_system_alarm_summary | 2 | 56 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 |  | BMS_FAULT | 系統故障 | summary_of_bms_system_faults | 2 | 57 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 |  | INPUT_IN0 | EPO觸發 | system_input_0 | 2 | 58 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 |  | TERMINAL_OVER_TEMP_SLIGHT | 終端高溫_輕微 | system_terminal_over_temperature_slight_alarm | 2 | 70 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 |  | TERMINAL_OVER_TEMP_MEDIUM | 終端高溫_中度 | system_terminal_over_temperature_medium_alarm | 2 | 71 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 |  | TERMINAL_OVER_TEMP_SERIOUS | 終端高溫_嚴重 | system_terminal_over_temperature_serious_alarm | 2 | 72 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 |  | MODULE_OVER_VOLT_SLIGHT | PACK過壓_輕微 | system_module_voltage_overvoltage_slight_alarm | 2 | 73 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 |  | MODULE_OVER_VOLT_MEDIUM | PACK過壓_中度 | system_module_voltage_overvoltage_medium_alarm | 2 | 74 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 |  | MODULE_OVER_VOLT_SERIOUS | PACK過壓_嚴重 | system_module_voltage_overvoltage_serious_alarm | 2 | 75 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 |  | MODULE_UNDER_VOLT_SLIGHT | PACK欠壓_輕微 | system_module_voltage_undervoltage_slight_alarm | 2 | 76 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 |  | MODULE_UNDER_VOLT_MEDIUM | PACK欠壓_中度 | system_module_voltage_undervoltage_medium_alarm | 2 | 77 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 |  | MODULE_UNDER_VOLT_SERIOUS | PACK欠壓_嚴重 | system_module_voltage_undervoltage_serious_alarm | 2 | 78 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 |  | CELL_VOLT_ACQ_FAULT | 電芯電壓抓取失敗 | system_cell_voltage_acquisition_fault | 2 | 79 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 |  | CELL_TEMP_ACQ_FAULT | 電芯溫度抓取失敗 | system_cell_temperature_acquisition_fault | 2 | 80 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,0 | RACK_LOST_COMM | 失去通訊 | rack_cbmu_lost_communication | 2 | 200 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,0 | UNDER_VOLT_SLIGHT | 欠壓_輕微 | rack_total_voltage_undervoltage_slight_alarm | 2 | 201 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,0 | UNDER_VOLT_MEDIUM | 欠壓_中度 | rack_total_voltage_undervoltage_medium_alarm | 2 | 202 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,0 | UNDER_VOLT_SERIOUS | 欠壓_嚴重 | rack_total_voltage_undervoltage_serious_alarm | 2 | 203 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,0 | OVER_VOLT_SLIGHT | 過壓_輕微 | rack_total_voltage_overvoltage_slight_alarm | 2 | 204 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,0 | OVER_VOLT_MEDIUM | 過壓_中度 | rack_total_voltage_overvoltage_medium_alarm | 2 | 205 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,0 | OVER_VOLT_SERIOUS | 過壓_嚴重 | rack_total_voltage_overvoltage_serious_alarm | 2 | 206 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,0 | OVER_CURRENT_SLIGHT | 過流_輕微 | rack_over_current_slight_alarm | 2 | 207 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,0 | OVER_CURRENT_MEDIUM | 過流_中度 | rack_over_current_medium_alarm | 2 | 208 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,0 | OVER_CURRENT_SERIOUS | 過流_嚴重 | rack_over_current_serious_alarm | 2 | 209 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,0 | CELL_UNDER_VOLT_SLIGHT | 電芯欠壓_輕微 | rack_cell_voltage_undervoltage_slight_alarm | 2 | 210 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,0 | CELL_UNDER_VOLT_MEDIUM | 電芯欠壓_中度 | rack_cell_voltage_undervoltage_medium_alarm | 2 | 211 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,0 | CELL_UNDER_VOLT_SERIOUS | 電芯欠壓_嚴重 | rack_cell_voltage_undervoltage_serious_alarm | 2 | 212 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,0 | CELL_OVER_VOLT_SLIGHT | 電芯過壓_輕微 | rack_cell_voltage_overvoltage_slight_alarm | 2 | 213 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,0 | CELL_OVER_VOLT_MEDIUM | 電芯過壓_中度 | rack_cell_voltage_overvoltage_medium_alarm | 2 | 214 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,0 | CELL_OVER_VOLT_SERIOUS | 電芯過壓_嚴重 | rack_cell_voltage_overvoltage_serious_alarm | 2 | 215 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,0 | CELL_LOW_TEMP_SLIGHT | 電芯低溫_輕微 | rack_cell_low_temperature_slight_alarm | 2 | 216 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,0 | CELL_LOW_TEMP_MEDIUM | 電芯低溫_中度 | rack_cell_low_temperature_medium_alarm | 2 | 217 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,0 | CELL_LOW_TEMP_SERIOUS | 電芯低溫_嚴重 | rack_cell_low_temperature_serious_alarm | 2 | 218 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,0 | CELL_OVER_TEMP_SLIGHT | 電芯高溫_輕微 | rack_cell_over_temperature_slight_alarm | 2 | 219 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,0 | CELL_OVER_TEMP_MEDIUM | 電芯高溫_中度 | rack_cell_over_temperature_medium_alarm | 2 | 220 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,0 | CELL_OVER_TEMP_SERIOUS | 電芯高溫_嚴重 | rack_cell_over_temperature_serious_alarm | 2 | 221 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,0 | CELL_SOC_LOW_SLIGHT | 電芯SOC過低_輕微 | rack_cell_soc_low_slight_alarm | 2 | 222 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,0 | CELL_SOC_LOW_MEDIUM | 電芯SOC過低_中度 | rack_cell_soc_low_medium_alarm | 2 | 223 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,0 | CELL_SOC_LOW_SERIOUS | 電芯SOC過低_嚴重 | rack_cell_soc_low_serious_alarm | 2 | 224 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,0 | CELL_SOC_HIGH_SLIGHT | 電芯SOC過高_輕微 | rack_cell_soc_high_slight_alarm | 2 | 225 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,0 | CELL_SOC_HIGH_MEDIUM | 電芯SOC過高_中度 | rack_cell_soc_high_medium_alarm | 2 | 226 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,0 | CELL_SOC_HIGH_SERIOUS | 電芯SOC過高_嚴重 | rack_cell_soc_high_serious_alarm | 2 | 227 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,0 | CELL_SOH_LOW_SLIGHT | 電芯SOH過低_輕微 | rack_cell_soh_low_slight_alarm | 2 | 228 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,0 | CELL_SOH_LOW_MEDIUM | 電芯SOH過低_中度 | rack_cell_soh_low_medium_alarm | 2 | 229 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,0 | CELL_SOH_LOW_SERIOUS | 電芯SOH過低_嚴重 | rack_cell_soh_low_serious_alarm | 2 | 230 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,0 | CELL_DIFF_VOLT_SLIGHT | 電芯壓差_輕微 | rack_cell_voltage_different_slight_alarm | 2 | 231 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,0 | CELL_DIFF_VOLT_MEDIUM | 電芯壓差_中度 | rack_cell_voltage_different_medium_alarm | 2 | 232 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,0 | CELL_DIFF_VOLT_SERIOUS | 電芯壓差_嚴重 | rack_cell_voltage_different_serious_alarm | 2 | 233 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,0 | CELL_DIFF_TEMP_SLIGHT | 電芯溫差_輕微 | rack_cell_temperature_different_slight_alarm | 2 | 234 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,0 | CELL_DIFF_TEMP_MEDIUM | 電芯溫差_中度 | rack_cell_temperature_different_medium_alarm | 2 | 235 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,0 | CELL_DIFF_TEMP_SERIOUS | 電芯溫差_嚴重 | rack_cell_temperature_different_serious_alarm | 2 | 236 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,0 | VT-BOARD_1_LOST_COMM | ESBMM_1_失去通信 | rack_v_t_measurement_board_1_lost_communication | 2 | 237 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,0 | VT-BOARD_2_LOST_COMM | ESBMM_2_失去通信 | rack_v_t_measurement_board_2_lost_communication | 2 | 238 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,0 | VT-BOARD_3_LOST_COMM | ESBMM_3_失去通信 | rack_v_t_measurement_board_3_lost_communication | 2 | 239 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,0 | VT-BOARD_4_LOST_COMM | ESBMM_4_失去通信 | rack_v_t_measurement_board_4_lost_communication | 2 | 240 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,0 | VT-BOARD_5_LOST_COMM | ESBMM_5_失去通信 | rack_v_t_measurement_board_5_lost_communication | 2 | 241 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,0 | VT-BOARD_6_LOST_COMM | ESBMM_6_失去通信 | rack_v_t_measurement_board_6_lost_communication | 2 | 242 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,0 | VT-BOARD_7_LOST_COMM | ESBMM_7_失去通信 | rack_v_t_measurement_board_7_lost_communication | 2 | 243 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,0 | VT-BOARD_8_LOST_COMM | ESBMM_8_失去通信 | rack_v_t_measurement_board_8_lost_communication | 2 | 244 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,0 | VT-BOARD_9_LOST_COMM | ESBMM_9_失去通信 | rack_v_t_measurement_board_9_lost_communication | 2 | 245 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,0 | VT-BOARD_10_LOST_COMM | ESBMM_10_失去通信 | rack_v_t_measurement_board_10_lost_communication | 2 | 246 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,0 | VT-BOARD_11_LOST_COMM | ESBMM_11_失去通信 | rack_v_t_measurement_board_11_lost_communication | 2 | 247 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,0 | VT-BOARD_12_LOST_COMM | ESBMM_12_失去通信 | rack_v_t_measurement_board_12_lost_communication | 2 | 248 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,0 | VT-BOARD_13_LOST_COMM | ESBMM_13_失去通信 | rack_v_t_measurement_board_13_lost_communication | 2 | 249 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,0 | VT-BOARD_14_LOST_COMM | ESBMM_14_失去通信 | rack_v_t_measurement_board_14_lost_communication | 2 | 250 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,0 | VT-BOARD_15_LOST_COMM | ESBMM_15_失去通信 | rack_v_t_measurement_board_15_lost_communication | 2 | 251 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,0 | VT-BOARD_16_LOST_COMM | ESBMM_16_失去通信 | rack_v_t_measurement_board_16_lost_communication | 2 | 252 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,0 | VT-BOARD_17_LOST_COMM | ESBMM_17_失去通信 | rack_v_t_measurement_board_17_lost_communication | 2 | 253 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,0 | VT-BOARD_18_LOST_COMM | ESBMM_18_失去通信 | rack_v_t_measurement_board_18_lost_communication | 2 | 254 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,0 | VT-BOARD_19_LOST_COMM | ESBMM_19_失去通信 | rack_v_t_measurement_board_19_lost_communication | 2 | 255 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,0 | VT-BOARD_20_LOST_COMM | ESBMM_20_失去通信 | rack_v_t_measurement_board_20_lost_communication | 2 | 256 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,0 | VT-BOARD_21_LOST_COMM | ESBMM_21_失去通信 | rack_v_t_measurement_board_21_lost_communication | 2 | 257 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,0 | VT-BOARD_22_LOST_COMM | ESBMM_22_失去通信 | rack_v_t_measurement_board_22_lost_communication | 2 | 258 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,0 | VT-BOARD_23_LOST_COMM | ESBMM_23_失去通信 | rack_v_t_measurement_board_23_lost_communication | 2 | 259 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,0 | VT-BOARD_24_LOST_COMM | ESBMM_24_失去通信 | rack_v_t_measurement_board_24_lost_communication | 2 | 260 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,0 | VT-BOARD_25_LOST_COMM | ESBMM_25_失去通信 | rack_v_t_measurement_board_25_lost_communication | 2 | 261 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,0 | VT-BOARD_26_LOST_COMM | ESBMM_26_失去通信 | rack_v_t_measurement_board_26_lost_communication | 2 | 262 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,0 | VT-BOARD_27_LOST_COMM | ESBMM_27_失去通信 | rack_v_t_measurement_board_27_lost_communication | 2 | 263 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,0 | VT-BOARD_28_LOST_COMM | ESBMM_28_失去通信 | rack_v_t_measurement_board_28_lost_communication | 2 | 264 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,0 | VT-BOARD_29_LOST_COMM | ESBMM_29_失去通信 | rack_v_t_measurement_board_29_lost_communication | 2 | 265 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,0 | VT-BOARD_30_LOST_COMM | ESBMM_30_失去通信 | rack_v_t_measurement_board_30_lost_communication | 2 | 266 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,0 | VT-BOARD_31_LOST_COMM | ESBMM_31_失去通信 | rack_v_t_measurement_board_31_lost_communication | 2 | 267 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,0 | VT-BOARD_32_LOST_COMM | ESBMM_32_失去通信 | rack_v_t_measurement_board_32_lost_communication | 2 | 268 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,0 | VT-BOARD_33_LOST_COMM | ESBMM_33_失去通信 | rack_v_t_measurement_board_33_lost_communication | 2 | 269 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,0 | VT-BOARD_34_LOST_COMM | ESBMM_34_失去通信 | rack_v_t_measurement_board_34_lost_communication | 2 | 270 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,0 | VT-BOARD_35_LOST_COMM | ESBMM_35_失去通信 | rack_v_t_measurement_board_35_lost_communication | 2 | 271 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,0 | VT-BOARD_36_LOST_COMM | ESBMM_36_失去通信 | rack_v_t_measurement_board_36_lost_communication | 2 | 272 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,0 | VT-BOARD_37_LOST_COMM | ESBMM_37_失去通信 | rack_v_t_measurement_board_37_lost_communication | 2 | 273 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,0 | VT-BOARD_38_LOST_COMM | ESBMM_38_失去通信 | rack_v_t_measurement_board_38_lost_communication | 2 | 274 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,0 | VT-BOARD_39_LOST_COMM | ESBMM_39_失去通信 | rack_v_t_measurement_board_39_lost_communication | 2 | 275 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,0 | VT-BOARD_40_LOST_COMM | ESBMM_40_失去通信 | rack_v_t_measurement_board_40_lost_communication | 2 | 276 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,0 | TERMINAL_HIGH_TEMP_SLIGHT | 終端高溫_輕微 | rack_terminal_temperature_high_slight_alarm | 2 | 277 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,0 | TERMINAL_HIGH_TEMP_MEDIUM | 終端高溫_中度 | rack_terminal_temperature_high_medium_alarm | 2 | 278 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,0 | TERMINAL_HIGH_TEMP_SERIOUS | 終端高溫_嚴重 | rack_terminal_temperature_high_serious_alarm | 2 | 279 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,0 | MODULE_OVER_VOLT_SLIGHT | PACK過壓_輕微 | rack_module_voltage_overvoltage_slight_alarm | 2 | 280 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,0 | MODULE_OVER_VOLT_MEDIUM | PACK過壓_中度 | rack_module_voltage_overvoltage_medium_alarm | 2 | 281 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,0 | MODULE_OVER_VOLT_SERIOUS | PACK過壓_嚴重 | rack_module_voltage_overvoltage_serious_alarm | 2 | 282 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,0 | MODULE_UNDER_VOLT_SLIGHT | PACK欠壓_輕微 | rack_module_voltage_undervoltage_slight_alarm | 2 | 283 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,0 | MODULE_UNDER_VOLT_MEDIUM | PACK欠壓_中度 | rack_module_voltage_undervoltage_medium_alarm | 2 | 284 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,0 | MODULE_UNDER_VOLT_SERIOUS | PACK欠壓_嚴重 | rack_module_voltage_undervoltage_serious_alarm | 2 | 285 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,0 | CELL_VOLT_ACQ_FAULT | 電芯電壓抓取失敗 | rack_cell_voltage_acquisition_fault | 2 | 286 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,0 | CELL_TEMP_ACQ_FAULT | 電芯溫度抓取失敗 | rack_cell_temperature_acquisition_fault | 2 | 287 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,1 | RACK_LOST_COMM | 失去通訊 | rack_cbmu_lost_communication | 2 | 300 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,1 | UNDER_VOLT_SLIGHT | 欠壓_輕微 | rack_total_voltage_undervoltage_slight_alarm | 2 | 301 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,1 | UNDER_VOLT_MEDIUM | 欠壓_中度 | rack_total_voltage_undervoltage_medium_alarm | 2 | 302 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,1 | UNDER_VOLT_SERIOUS | 欠壓_嚴重 | rack_total_voltage_undervoltage_serious_alarm | 2 | 303 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,1 | OVER_VOLT_SLIGHT | 過壓_輕微 | rack_total_voltage_overvoltage_slight_alarm | 2 | 304 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,1 | OVER_VOLT_MEDIUM | 過壓_中度 | rack_total_voltage_overvoltage_medium_alarm | 2 | 305 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,1 | OVER_VOLT_SERIOUS | 過壓_嚴重 | rack_total_voltage_overvoltage_serious_alarm | 2 | 306 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,1 | OVER_CURRENT_SLIGHT | 過流_輕微 | rack_over_current_slight_alarm | 2 | 307 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,1 | OVER_CURRENT_MEDIUM | 過流_中度 | rack_over_current_medium_alarm | 2 | 308 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,1 | OVER_CURRENT_SERIOUS | 過流_嚴重 | rack_over_current_serious_alarm | 2 | 309 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,1 | CELL_UNDER_VOLT_SLIGHT | 電芯欠壓_輕微 | rack_cell_voltage_undervoltage_slight_alarm | 2 | 310 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,1 | CELL_UNDER_VOLT_MEDIUM | 電芯欠壓_中度 | rack_cell_voltage_undervoltage_medium_alarm | 2 | 311 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,1 | CELL_UNDER_VOLT_SERIOUS | 電芯欠壓_嚴重 | rack_cell_voltage_undervoltage_serious_alarm | 2 | 312 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,1 | CELL_OVER_VOLT_SLIGHT | 電芯過壓_輕微 | rack_cell_voltage_overvoltage_slight_alarm | 2 | 313 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,1 | CELL_OVER_VOLT_MEDIUM | 電芯過壓_中度 | rack_cell_voltage_overvoltage_medium_alarm | 2 | 314 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,1 | CELL_OVER_VOLT_SERIOUS | 電芯過壓_嚴重 | rack_cell_voltage_overvoltage_serious_alarm | 2 | 315 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,1 | CELL_LOW_TEMP_SLIGHT | 電芯低溫_輕微 | rack_cell_low_temperature_slight_alarm | 2 | 316 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,1 | CELL_LOW_TEMP_MEDIUM | 電芯低溫_中度 | rack_cell_low_temperature_medium_alarm | 2 | 317 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,1 | CELL_LOW_TEMP_SERIOUS | 電芯低溫_嚴重 | rack_cell_low_temperature_serious_alarm | 2 | 318 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,1 | CELL_OVER_TEMP_SLIGHT | 電芯高溫_輕微 | rack_cell_over_temperature_slight_alarm | 2 | 319 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,1 | CELL_OVER_TEMP_MEDIUM | 電芯高溫_中度 | rack_cell_over_temperature_medium_alarm | 2 | 320 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,1 | CELL_OVER_TEMP_SERIOUS | 電芯高溫_嚴重 | rack_cell_over_temperature_serious_alarm | 2 | 321 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,1 | CELL_SOC_LOW_SLIGHT | 電芯SOC過低_輕微 | rack_cell_soc_low_slight_alarm | 2 | 322 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,1 | CELL_SOC_LOW_MEDIUM | 電芯SOC過低_中度 | rack_cell_soc_low_medium_alarm | 2 | 323 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,1 | CELL_SOC_LOW_SERIOUS | 電芯SOC過低_嚴重 | rack_cell_soc_low_serious_alarm | 2 | 324 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,1 | CELL_SOC_HIGH_SLIGHT | 電芯SOC過高_輕微 | rack_cell_soc_high_slight_alarm | 2 | 325 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,1 | CELL_SOC_HIGH_MEDIUM | 電芯SOC過高_中度 | rack_cell_soc_high_medium_alarm | 2 | 326 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,1 | CELL_SOC_HIGH_SERIOUS | 電芯SOC過高_嚴重 | rack_cell_soc_high_serious_alarm | 2 | 327 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,1 | CELL_SOH_LOW_SLIGHT | 電芯SOH過低_輕微 | rack_cell_soh_low_slight_alarm | 2 | 328 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,1 | CELL_SOH_LOW_MEDIUM | 電芯SOH過低_中度 | rack_cell_soh_low_medium_alarm | 2 | 329 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,1 | CELL_SOH_LOW_SERIOUS | 電芯SOH過低_嚴重 | rack_cell_soh_low_serious_alarm | 2 | 330 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,1 | CELL_DIFF_VOLT_SLIGHT | 電芯壓差_輕微 | rack_cell_voltage_different_slight_alarm | 2 | 331 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,1 | CELL_DIFF_VOLT_MEDIUM | 電芯壓差_中度 | rack_cell_voltage_different_medium_alarm | 2 | 332 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,1 | CELL_DIFF_VOLT_SERIOUS | 電芯壓差_嚴重 | rack_cell_voltage_different_serious_alarm | 2 | 333 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,1 | CELL_DIFF_TEMP_SLIGHT | 電芯溫差_輕微 | rack_cell_temperature_different_slight_alarm | 2 | 334 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,1 | CELL_DIFF_TEMP_MEDIUM | 電芯溫差_中度 | rack_cell_temperature_different_medium_alarm | 2 | 335 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,1 | CELL_DIFF_TEMP_SERIOUS | 電芯溫差_嚴重 | rack_cell_temperature_different_serious_alarm | 2 | 336 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,1 | VT-BOARD_1_LOST_COMM | ESBMM_1_失去通信 | rack_v_t_measurement_board_1_lost_communication | 2 | 337 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,1 | VT-BOARD_2_LOST_COMM | ESBMM_2_失去通信 | rack_v_t_measurement_board_2_lost_communication | 2 | 338 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,1 | VT-BOARD_3_LOST_COMM | ESBMM_3_失去通信 | rack_v_t_measurement_board_3_lost_communication | 2 | 339 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,1 | VT-BOARD_4_LOST_COMM | ESBMM_4_失去通信 | rack_v_t_measurement_board_4_lost_communication | 2 | 340 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,1 | VT-BOARD_5_LOST_COMM | ESBMM_5_失去通信 | rack_v_t_measurement_board_5_lost_communication | 2 | 341 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,1 | VT-BOARD_6_LOST_COMM | ESBMM_6_失去通信 | rack_v_t_measurement_board_6_lost_communication | 2 | 342 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,1 | VT-BOARD_7_LOST_COMM | ESBMM_7_失去通信 | rack_v_t_measurement_board_7_lost_communication | 2 | 343 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,1 | VT-BOARD_8_LOST_COMM | ESBMM_8_失去通信 | rack_v_t_measurement_board_8_lost_communication | 2 | 344 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,1 | VT-BOARD_9_LOST_COMM | ESBMM_9_失去通信 | rack_v_t_measurement_board_9_lost_communication | 2 | 345 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,1 | VT-BOARD_10_LOST_COMM | ESBMM_10_失去通信 | rack_v_t_measurement_board_10_lost_communication | 2 | 346 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,1 | VT-BOARD_11_LOST_COMM | ESBMM_11_失去通信 | rack_v_t_measurement_board_11_lost_communication | 2 | 347 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,1 | VT-BOARD_12_LOST_COMM | ESBMM_12_失去通信 | rack_v_t_measurement_board_12_lost_communication | 2 | 348 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,1 | VT-BOARD_13_LOST_COMM | ESBMM_13_失去通信 | rack_v_t_measurement_board_13_lost_communication | 2 | 349 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,1 | VT-BOARD_14_LOST_COMM | ESBMM_14_失去通信 | rack_v_t_measurement_board_14_lost_communication | 2 | 350 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,1 | VT-BOARD_15_LOST_COMM | ESBMM_15_失去通信 | rack_v_t_measurement_board_15_lost_communication | 2 | 351 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,1 | VT-BOARD_16_LOST_COMM | ESBMM_16_失去通信 | rack_v_t_measurement_board_16_lost_communication | 2 | 352 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,1 | VT-BOARD_17_LOST_COMM | ESBMM_17_失去通信 | rack_v_t_measurement_board_17_lost_communication | 2 | 353 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,1 | VT-BOARD_18_LOST_COMM | ESBMM_18_失去通信 | rack_v_t_measurement_board_18_lost_communication | 2 | 354 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,1 | VT-BOARD_19_LOST_COMM | ESBMM_19_失去通信 | rack_v_t_measurement_board_19_lost_communication | 2 | 355 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,1 | VT-BOARD_20_LOST_COMM | ESBMM_20_失去通信 | rack_v_t_measurement_board_20_lost_communication | 2 | 356 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,1 | VT-BOARD_21_LOST_COMM | ESBMM_21_失去通信 | rack_v_t_measurement_board_21_lost_communication | 2 | 357 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,1 | VT-BOARD_22_LOST_COMM | ESBMM_22_失去通信 | rack_v_t_measurement_board_22_lost_communication | 2 | 358 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,1 | VT-BOARD_23_LOST_COMM | ESBMM_23_失去通信 | rack_v_t_measurement_board_23_lost_communication | 2 | 359 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,1 | VT-BOARD_24_LOST_COMM | ESBMM_24_失去通信 | rack_v_t_measurement_board_24_lost_communication | 2 | 360 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,1 | VT-BOARD_25_LOST_COMM | ESBMM_25_失去通信 | rack_v_t_measurement_board_25_lost_communication | 2 | 361 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,1 | VT-BOARD_26_LOST_COMM | ESBMM_26_失去通信 | rack_v_t_measurement_board_26_lost_communication | 2 | 362 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,1 | VT-BOARD_27_LOST_COMM | ESBMM_27_失去通信 | rack_v_t_measurement_board_27_lost_communication | 2 | 363 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,1 | VT-BOARD_28_LOST_COMM | ESBMM_28_失去通信 | rack_v_t_measurement_board_28_lost_communication | 2 | 364 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,1 | VT-BOARD_29_LOST_COMM | ESBMM_29_失去通信 | rack_v_t_measurement_board_29_lost_communication | 2 | 365 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,1 | VT-BOARD_30_LOST_COMM | ESBMM_30_失去通信 | rack_v_t_measurement_board_30_lost_communication | 2 | 366 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,1 | VT-BOARD_31_LOST_COMM | ESBMM_31_失去通信 | rack_v_t_measurement_board_31_lost_communication | 2 | 367 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,1 | VT-BOARD_32_LOST_COMM | ESBMM_32_失去通信 | rack_v_t_measurement_board_32_lost_communication | 2 | 368 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,1 | VT-BOARD_33_LOST_COMM | ESBMM_33_失去通信 | rack_v_t_measurement_board_33_lost_communication | 2 | 369 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,1 | VT-BOARD_34_LOST_COMM | ESBMM_34_失去通信 | rack_v_t_measurement_board_34_lost_communication | 2 | 370 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,1 | VT-BOARD_35_LOST_COMM | ESBMM_35_失去通信 | rack_v_t_measurement_board_35_lost_communication | 2 | 371 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,1 | VT-BOARD_36_LOST_COMM | ESBMM_36_失去通信 | rack_v_t_measurement_board_36_lost_communication | 2 | 372 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,1 | VT-BOARD_37_LOST_COMM | ESBMM_37_失去通信 | rack_v_t_measurement_board_37_lost_communication | 2 | 373 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,1 | VT-BOARD_38_LOST_COMM | ESBMM_38_失去通信 | rack_v_t_measurement_board_38_lost_communication | 2 | 374 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,1 | VT-BOARD_39_LOST_COMM | ESBMM_39_失去通信 | rack_v_t_measurement_board_39_lost_communication | 2 | 375 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,1 | VT-BOARD_40_LOST_COMM | ESBMM_40_失去通信 | rack_v_t_measurement_board_40_lost_communication | 2 | 376 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,1 | TERMINAL_HIGH_TEMP_SLIGHT | 終端高溫_輕微 | rack_terminal_temperature_high_slight_alarm | 2 | 377 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,1 | TERMINAL_HIGH_TEMP_MEDIUM | 終端高溫_中度 | rack_terminal_temperature_high_medium_alarm | 2 | 378 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,1 | TERMINAL_HIGH_TEMP_SERIOUS | 終端高溫_嚴重 | rack_terminal_temperature_high_serious_alarm | 2 | 379 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,1 | MODULE_OVER_VOLT_SLIGHT | PACK過壓_輕微 | rack_module_voltage_overvoltage_slight_alarm | 2 | 380 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,1 | MODULE_OVER_VOLT_MEDIUM | PACK過壓_中度 | rack_module_voltage_overvoltage_medium_alarm | 2 | 381 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,1 | MODULE_OVER_VOLT_SERIOUS | PACK過壓_嚴重 | rack_module_voltage_overvoltage_serious_alarm | 2 | 382 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,1 | MODULE_UNDER_VOLT_SLIGHT | PACK欠壓_輕微 | rack_module_voltage_undervoltage_slight_alarm | 2 | 383 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,1 | MODULE_UNDER_VOLT_MEDIUM | PACK欠壓_中度 | rack_module_voltage_undervoltage_medium_alarm | 2 | 384 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,1 | MODULE_UNDER_VOLT_SERIOUS | PACK欠壓_嚴重 | rack_module_voltage_undervoltage_serious_alarm | 2 | 385 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,1 | CELL_VOLT_ACQ_FAULT | 電芯電壓抓取失敗 | rack_cell_voltage_acquisition_fault | 2 | 386 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,1 | CELL_TEMP_ACQ_FAULT | 電芯溫度抓取失敗 | rack_cell_temperature_acquisition_fault | 2 | 387 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,2 | RACK_LOST_COMM | 失去通訊 | rack_cbmu_lost_communication | 2 | 400 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,2 | UNDER_VOLT_SLIGHT | 欠壓_輕微 | rack_total_voltage_undervoltage_slight_alarm | 2 | 401 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,2 | UNDER_VOLT_MEDIUM | 欠壓_中度 | rack_total_voltage_undervoltage_medium_alarm | 2 | 402 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,2 | UNDER_VOLT_SERIOUS | 欠壓_嚴重 | rack_total_voltage_undervoltage_serious_alarm | 2 | 403 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,2 | OVER_VOLT_SLIGHT | 過壓_輕微 | rack_total_voltage_overvoltage_slight_alarm | 2 | 404 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,2 | OVER_VOLT_MEDIUM | 過壓_中度 | rack_total_voltage_overvoltage_medium_alarm | 2 | 405 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,2 | OVER_VOLT_SERIOUS | 過壓_嚴重 | rack_total_voltage_overvoltage_serious_alarm | 2 | 406 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,2 | OVER_CURRENT_SLIGHT | 過流_輕微 | rack_over_current_slight_alarm | 2 | 407 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,2 | OVER_CURRENT_MEDIUM | 過流_中度 | rack_over_current_medium_alarm | 2 | 408 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,2 | OVER_CURRENT_SERIOUS | 過流_嚴重 | rack_over_current_serious_alarm | 2 | 409 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,2 | CELL_UNDER_VOLT_SLIGHT | 電芯欠壓_輕微 | rack_cell_voltage_undervoltage_slight_alarm | 2 | 410 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,2 | CELL_UNDER_VOLT_MEDIUM | 電芯欠壓_中度 | rack_cell_voltage_undervoltage_medium_alarm | 2 | 411 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,2 | CELL_UNDER_VOLT_SERIOUS | 電芯欠壓_嚴重 | rack_cell_voltage_undervoltage_serious_alarm | 2 | 412 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,2 | CELL_OVER_VOLT_SLIGHT | 電芯過壓_輕微 | rack_cell_voltage_overvoltage_slight_alarm | 2 | 413 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,2 | CELL_OVER_VOLT_MEDIUM | 電芯過壓_中度 | rack_cell_voltage_overvoltage_medium_alarm | 2 | 414 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,2 | CELL_OVER_VOLT_SERIOUS | 電芯過壓_嚴重 | rack_cell_voltage_overvoltage_serious_alarm | 2 | 415 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,2 | CELL_LOW_TEMP_SLIGHT | 電芯低溫_輕微 | rack_cell_low_temperature_slight_alarm | 2 | 416 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,2 | CELL_LOW_TEMP_MEDIUM | 電芯低溫_中度 | rack_cell_low_temperature_medium_alarm | 2 | 417 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,2 | CELL_LOW_TEMP_SERIOUS | 電芯低溫_嚴重 | rack_cell_low_temperature_serious_alarm | 2 | 418 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,2 | CELL_OVER_TEMP_SLIGHT | 電芯高溫_輕微 | rack_cell_over_temperature_slight_alarm | 2 | 419 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,2 | CELL_OVER_TEMP_MEDIUM | 電芯高溫_中度 | rack_cell_over_temperature_medium_alarm | 2 | 420 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,2 | CELL_OVER_TEMP_SERIOUS | 電芯高溫_嚴重 | rack_cell_over_temperature_serious_alarm | 2 | 421 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,2 | CELL_SOC_LOW_SLIGHT | 電芯SOC過低_輕微 | rack_cell_soc_low_slight_alarm | 2 | 422 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,2 | CELL_SOC_LOW_MEDIUM | 電芯SOC過低_中度 | rack_cell_soc_low_medium_alarm | 2 | 423 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,2 | CELL_SOC_LOW_SERIOUS | 電芯SOC過低_嚴重 | rack_cell_soc_low_serious_alarm | 2 | 424 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,2 | CELL_SOC_HIGH_SLIGHT | 電芯SOC過高_輕微 | rack_cell_soc_high_slight_alarm | 2 | 425 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,2 | CELL_SOC_HIGH_MEDIUM | 電芯SOC過高_中度 | rack_cell_soc_high_medium_alarm | 2 | 426 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,2 | CELL_SOC_HIGH_SERIOUS | 電芯SOC過高_嚴重 | rack_cell_soc_high_serious_alarm | 2 | 427 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,2 | CELL_SOH_LOW_SLIGHT | 電芯SOH過低_輕微 | rack_cell_soh_low_slight_alarm | 2 | 428 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,2 | CELL_SOH_LOW_MEDIUM | 電芯SOH過低_中度 | rack_cell_soh_low_medium_alarm | 2 | 429 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,2 | CELL_SOH_LOW_SERIOUS | 電芯SOH過低_嚴重 | rack_cell_soh_low_serious_alarm | 2 | 430 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,2 | CELL_DIFF_VOLT_SLIGHT | 電芯壓差_輕微 | rack_cell_voltage_different_slight_alarm | 2 | 431 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,2 | CELL_DIFF_VOLT_MEDIUM | 電芯壓差_中度 | rack_cell_voltage_different_medium_alarm | 2 | 432 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,2 | CELL_DIFF_VOLT_SERIOUS | 電芯壓差_嚴重 | rack_cell_voltage_different_serious_alarm | 2 | 433 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,2 | CELL_DIFF_TEMP_SLIGHT | 電芯溫差_輕微 | rack_cell_temperature_different_slight_alarm | 2 | 434 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,2 | CELL_DIFF_TEMP_MEDIUM | 電芯溫差_中度 | rack_cell_temperature_different_medium_alarm | 2 | 435 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,2 | CELL_DIFF_TEMP_SERIOUS | 電芯溫差_嚴重 | rack_cell_temperature_different_serious_alarm | 2 | 436 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,2 | VT-BOARD_1_LOST_COMM | ESBMM_1_失去通信 | rack_v_t_measurement_board_1_lost_communication | 2 | 437 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,2 | VT-BOARD_2_LOST_COMM | ESBMM_2_失去通信 | rack_v_t_measurement_board_2_lost_communication | 2 | 438 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,2 | VT-BOARD_3_LOST_COMM | ESBMM_3_失去通信 | rack_v_t_measurement_board_3_lost_communication | 2 | 439 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,2 | VT-BOARD_4_LOST_COMM | ESBMM_4_失去通信 | rack_v_t_measurement_board_4_lost_communication | 2 | 440 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,2 | VT-BOARD_5_LOST_COMM | ESBMM_5_失去通信 | rack_v_t_measurement_board_5_lost_communication | 2 | 441 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,2 | VT-BOARD_6_LOST_COMM | ESBMM_6_失去通信 | rack_v_t_measurement_board_6_lost_communication | 2 | 442 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,2 | VT-BOARD_7_LOST_COMM | ESBMM_7_失去通信 | rack_v_t_measurement_board_7_lost_communication | 2 | 443 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,2 | VT-BOARD_8_LOST_COMM | ESBMM_8_失去通信 | rack_v_t_measurement_board_8_lost_communication | 2 | 444 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,2 | VT-BOARD_9_LOST_COMM | ESBMM_9_失去通信 | rack_v_t_measurement_board_9_lost_communication | 2 | 445 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,2 | VT-BOARD_10_LOST_COMM | ESBMM_10_失去通信 | rack_v_t_measurement_board_10_lost_communication | 2 | 446 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,2 | VT-BOARD_11_LOST_COMM | ESBMM_11_失去通信 | rack_v_t_measurement_board_11_lost_communication | 2 | 447 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,2 | VT-BOARD_12_LOST_COMM | ESBMM_12_失去通信 | rack_v_t_measurement_board_12_lost_communication | 2 | 448 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,2 | VT-BOARD_13_LOST_COMM | ESBMM_13_失去通信 | rack_v_t_measurement_board_13_lost_communication | 2 | 449 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,2 | VT-BOARD_14_LOST_COMM | ESBMM_14_失去通信 | rack_v_t_measurement_board_14_lost_communication | 2 | 450 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,2 | VT-BOARD_15_LOST_COMM | ESBMM_15_失去通信 | rack_v_t_measurement_board_15_lost_communication | 2 | 451 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,2 | VT-BOARD_16_LOST_COMM | ESBMM_16_失去通信 | rack_v_t_measurement_board_16_lost_communication | 2 | 452 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,2 | VT-BOARD_17_LOST_COMM | ESBMM_17_失去通信 | rack_v_t_measurement_board_17_lost_communication | 2 | 453 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,2 | VT-BOARD_18_LOST_COMM | ESBMM_18_失去通信 | rack_v_t_measurement_board_18_lost_communication | 2 | 454 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,2 | VT-BOARD_19_LOST_COMM | ESBMM_19_失去通信 | rack_v_t_measurement_board_19_lost_communication | 2 | 455 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,2 | VT-BOARD_20_LOST_COMM | ESBMM_20_失去通信 | rack_v_t_measurement_board_20_lost_communication | 2 | 456 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,2 | VT-BOARD_21_LOST_COMM | ESBMM_21_失去通信 | rack_v_t_measurement_board_21_lost_communication | 2 | 457 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,2 | VT-BOARD_22_LOST_COMM | ESBMM_22_失去通信 | rack_v_t_measurement_board_22_lost_communication | 2 | 458 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,2 | VT-BOARD_23_LOST_COMM | ESBMM_23_失去通信 | rack_v_t_measurement_board_23_lost_communication | 2 | 459 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,2 | VT-BOARD_24_LOST_COMM | ESBMM_24_失去通信 | rack_v_t_measurement_board_24_lost_communication | 2 | 460 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,2 | VT-BOARD_25_LOST_COMM | ESBMM_25_失去通信 | rack_v_t_measurement_board_25_lost_communication | 2 | 461 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,2 | VT-BOARD_26_LOST_COMM | ESBMM_26_失去通信 | rack_v_t_measurement_board_26_lost_communication | 2 | 462 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,2 | VT-BOARD_27_LOST_COMM | ESBMM_27_失去通信 | rack_v_t_measurement_board_27_lost_communication | 2 | 463 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,2 | VT-BOARD_28_LOST_COMM | ESBMM_28_失去通信 | rack_v_t_measurement_board_28_lost_communication | 2 | 464 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,2 | VT-BOARD_29_LOST_COMM | ESBMM_29_失去通信 | rack_v_t_measurement_board_29_lost_communication | 2 | 465 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,2 | VT-BOARD_30_LOST_COMM | ESBMM_30_失去通信 | rack_v_t_measurement_board_30_lost_communication | 2 | 466 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,2 | VT-BOARD_31_LOST_COMM | ESBMM_31_失去通信 | rack_v_t_measurement_board_31_lost_communication | 2 | 467 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,2 | VT-BOARD_32_LOST_COMM | ESBMM_32_失去通信 | rack_v_t_measurement_board_32_lost_communication | 2 | 468 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,2 | VT-BOARD_33_LOST_COMM | ESBMM_33_失去通信 | rack_v_t_measurement_board_33_lost_communication | 2 | 469 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,2 | VT-BOARD_34_LOST_COMM | ESBMM_34_失去通信 | rack_v_t_measurement_board_34_lost_communication | 2 | 470 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,2 | VT-BOARD_35_LOST_COMM | ESBMM_35_失去通信 | rack_v_t_measurement_board_35_lost_communication | 2 | 471 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,2 | VT-BOARD_36_LOST_COMM | ESBMM_36_失去通信 | rack_v_t_measurement_board_36_lost_communication | 2 | 472 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,2 | VT-BOARD_37_LOST_COMM | ESBMM_37_失去通信 | rack_v_t_measurement_board_37_lost_communication | 2 | 473 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,2 | VT-BOARD_38_LOST_COMM | ESBMM_38_失去通信 | rack_v_t_measurement_board_38_lost_communication | 2 | 474 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,2 | VT-BOARD_39_LOST_COMM | ESBMM_39_失去通信 | rack_v_t_measurement_board_39_lost_communication | 2 | 475 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,2 | VT-BOARD_40_LOST_COMM | ESBMM_40_失去通信 | rack_v_t_measurement_board_40_lost_communication | 2 | 476 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,2 | TERMINAL_HIGH_TEMP_SLIGHT | 終端高溫_輕微 | rack_terminal_temperature_high_slight_alarm | 2 | 477 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,2 | TERMINAL_HIGH_TEMP_MEDIUM | 終端高溫_中度 | rack_terminal_temperature_high_medium_alarm | 2 | 478 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,2 | TERMINAL_HIGH_TEMP_SERIOUS | 終端高溫_嚴重 | rack_terminal_temperature_high_serious_alarm | 2 | 479 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,2 | MODULE_OVER_VOLT_SLIGHT | PACK過壓_輕微 | rack_module_voltage_overvoltage_slight_alarm | 2 | 480 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,2 | MODULE_OVER_VOLT_MEDIUM | PACK過壓_中度 | rack_module_voltage_overvoltage_medium_alarm | 2 | 481 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,2 | MODULE_OVER_VOLT_SERIOUS | PACK過壓_嚴重 | rack_module_voltage_overvoltage_serious_alarm | 2 | 482 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,2 | MODULE_UNDER_VOLT_SLIGHT | PACK欠壓_輕微 | rack_module_voltage_undervoltage_slight_alarm | 2 | 483 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,2 | MODULE_UNDER_VOLT_MEDIUM | PACK欠壓_中度 | rack_module_voltage_undervoltage_medium_alarm | 2 | 484 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,2 | MODULE_UNDER_VOLT_SERIOUS | PACK欠壓_嚴重 | rack_module_voltage_undervoltage_serious_alarm | 2 | 485 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,2 | CELL_VOLT_ACQ_FAULT | 電芯電壓抓取失敗 | rack_cell_voltage_acquisition_fault | 2 | 486 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,2 | CELL_TEMP_ACQ_FAULT | 電芯溫度抓取失敗 | rack_cell_temperature_acquisition_fault | 2 | 487 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,3 | RACK_LOST_COMM | 失去通訊 | rack_cbmu_lost_communication | 2 | 500 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,3 | UNDER_VOLT_SLIGHT | 欠壓_輕微 | rack_total_voltage_undervoltage_slight_alarm | 2 | 501 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,3 | UNDER_VOLT_MEDIUM | 欠壓_中度 | rack_total_voltage_undervoltage_medium_alarm | 2 | 502 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,3 | UNDER_VOLT_SERIOUS | 欠壓_嚴重 | rack_total_voltage_undervoltage_serious_alarm | 2 | 503 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,3 | OVER_VOLT_SLIGHT | 過壓_輕微 | rack_total_voltage_overvoltage_slight_alarm | 2 | 504 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,3 | OVER_VOLT_MEDIUM | 過壓_中度 | rack_total_voltage_overvoltage_medium_alarm | 2 | 505 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,3 | OVER_VOLT_SERIOUS | 過壓_嚴重 | rack_total_voltage_overvoltage_serious_alarm | 2 | 506 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,3 | OVER_CURRENT_SLIGHT | 過流_輕微 | rack_over_current_slight_alarm | 2 | 507 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,3 | OVER_CURRENT_MEDIUM | 過流_中度 | rack_over_current_medium_alarm | 2 | 508 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,3 | OVER_CURRENT_SERIOUS | 過流_嚴重 | rack_over_current_serious_alarm | 2 | 509 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,3 | CELL_UNDER_VOLT_SLIGHT | 電芯欠壓_輕微 | rack_cell_voltage_undervoltage_slight_alarm | 2 | 510 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,3 | CELL_UNDER_VOLT_MEDIUM | 電芯欠壓_中度 | rack_cell_voltage_undervoltage_medium_alarm | 2 | 511 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,3 | CELL_UNDER_VOLT_SERIOUS | 電芯欠壓_嚴重 | rack_cell_voltage_undervoltage_serious_alarm | 2 | 512 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,3 | CELL_OVER_VOLT_SLIGHT | 電芯過壓_輕微 | rack_cell_voltage_overvoltage_slight_alarm | 2 | 513 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,3 | CELL_OVER_VOLT_MEDIUM | 電芯過壓_中度 | rack_cell_voltage_overvoltage_medium_alarm | 2 | 514 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,3 | CELL_OVER_VOLT_SERIOUS | 電芯過壓_嚴重 | rack_cell_voltage_overvoltage_serious_alarm | 2 | 515 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,3 | CELL_LOW_TEMP_SLIGHT | 電芯低溫_輕微 | rack_cell_low_temperature_slight_alarm | 2 | 516 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,3 | CELL_LOW_TEMP_MEDIUM | 電芯低溫_中度 | rack_cell_low_temperature_medium_alarm | 2 | 517 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,3 | CELL_LOW_TEMP_SERIOUS | 電芯低溫_嚴重 | rack_cell_low_temperature_serious_alarm | 2 | 518 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,3 | CELL_OVER_TEMP_SLIGHT | 電芯高溫_輕微 | rack_cell_over_temperature_slight_alarm | 2 | 519 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,3 | CELL_OVER_TEMP_MEDIUM | 電芯高溫_中度 | rack_cell_over_temperature_medium_alarm | 2 | 520 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,3 | CELL_OVER_TEMP_SERIOUS | 電芯高溫_嚴重 | rack_cell_over_temperature_serious_alarm | 2 | 521 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,3 | CELL_SOC_LOW_SLIGHT | 電芯SOC過低_輕微 | rack_cell_soc_low_slight_alarm | 2 | 522 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,3 | CELL_SOC_LOW_MEDIUM | 電芯SOC過低_中度 | rack_cell_soc_low_medium_alarm | 2 | 523 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,3 | CELL_SOC_LOW_SERIOUS | 電芯SOC過低_嚴重 | rack_cell_soc_low_serious_alarm | 2 | 524 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,3 | CELL_SOC_HIGH_SLIGHT | 電芯SOC過高_輕微 | rack_cell_soc_high_slight_alarm | 2 | 525 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,3 | CELL_SOC_HIGH_MEDIUM | 電芯SOC過高_中度 | rack_cell_soc_high_medium_alarm | 2 | 526 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,3 | CELL_SOC_HIGH_SERIOUS | 電芯SOC過高_嚴重 | rack_cell_soc_high_serious_alarm | 2 | 527 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,3 | CELL_SOH_LOW_SLIGHT | 電芯SOH過低_輕微 | rack_cell_soh_low_slight_alarm | 2 | 528 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,3 | CELL_SOH_LOW_MEDIUM | 電芯SOH過低_中度 | rack_cell_soh_low_medium_alarm | 2 | 529 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,3 | CELL_SOH_LOW_SERIOUS | 電芯SOH過低_嚴重 | rack_cell_soh_low_serious_alarm | 2 | 530 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,3 | CELL_DIFF_VOLT_SLIGHT | 電芯壓差_輕微 | rack_cell_voltage_different_slight_alarm | 2 | 531 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,3 | CELL_DIFF_VOLT_MEDIUM | 電芯壓差_中度 | rack_cell_voltage_different_medium_alarm | 2 | 532 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,3 | CELL_DIFF_VOLT_SERIOUS | 電芯壓差_嚴重 | rack_cell_voltage_different_serious_alarm | 2 | 533 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,3 | CELL_DIFF_TEMP_SLIGHT | 電芯溫差_輕微 | rack_cell_temperature_different_slight_alarm | 2 | 534 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,3 | CELL_DIFF_TEMP_MEDIUM | 電芯溫差_中度 | rack_cell_temperature_different_medium_alarm | 2 | 535 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,3 | CELL_DIFF_TEMP_SERIOUS | 電芯溫差_嚴重 | rack_cell_temperature_different_serious_alarm | 2 | 536 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,3 | VT-BOARD_1_LOST_COMM | ESBMM_1_失去通信 | rack_v_t_measurement_board_1_lost_communication | 2 | 537 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,3 | VT-BOARD_2_LOST_COMM | ESBMM_2_失去通信 | rack_v_t_measurement_board_2_lost_communication | 2 | 538 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,3 | VT-BOARD_3_LOST_COMM | ESBMM_3_失去通信 | rack_v_t_measurement_board_3_lost_communication | 2 | 539 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,3 | VT-BOARD_4_LOST_COMM | ESBMM_4_失去通信 | rack_v_t_measurement_board_4_lost_communication | 2 | 540 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,3 | VT-BOARD_5_LOST_COMM | ESBMM_5_失去通信 | rack_v_t_measurement_board_5_lost_communication | 2 | 541 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,3 | VT-BOARD_6_LOST_COMM | ESBMM_6_失去通信 | rack_v_t_measurement_board_6_lost_communication | 2 | 542 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,3 | VT-BOARD_7_LOST_COMM | ESBMM_7_失去通信 | rack_v_t_measurement_board_7_lost_communication | 2 | 543 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,3 | VT-BOARD_8_LOST_COMM | ESBMM_8_失去通信 | rack_v_t_measurement_board_8_lost_communication | 2 | 544 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,3 | VT-BOARD_9_LOST_COMM | ESBMM_9_失去通信 | rack_v_t_measurement_board_9_lost_communication | 2 | 545 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,3 | VT-BOARD_10_LOST_COMM | ESBMM_10_失去通信 | rack_v_t_measurement_board_10_lost_communication | 2 | 546 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,3 | VT-BOARD_11_LOST_COMM | ESBMM_11_失去通信 | rack_v_t_measurement_board_11_lost_communication | 2 | 547 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,3 | VT-BOARD_12_LOST_COMM | ESBMM_12_失去通信 | rack_v_t_measurement_board_12_lost_communication | 2 | 548 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,3 | VT-BOARD_13_LOST_COMM | ESBMM_13_失去通信 | rack_v_t_measurement_board_13_lost_communication | 2 | 549 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,3 | VT-BOARD_14_LOST_COMM | ESBMM_14_失去通信 | rack_v_t_measurement_board_14_lost_communication | 2 | 550 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,3 | VT-BOARD_15_LOST_COMM | ESBMM_15_失去通信 | rack_v_t_measurement_board_15_lost_communication | 2 | 551 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,3 | VT-BOARD_16_LOST_COMM | ESBMM_16_失去通信 | rack_v_t_measurement_board_16_lost_communication | 2 | 552 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,3 | VT-BOARD_17_LOST_COMM | ESBMM_17_失去通信 | rack_v_t_measurement_board_17_lost_communication | 2 | 553 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,3 | VT-BOARD_18_LOST_COMM | ESBMM_18_失去通信 | rack_v_t_measurement_board_18_lost_communication | 2 | 554 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,3 | VT-BOARD_19_LOST_COMM | ESBMM_19_失去通信 | rack_v_t_measurement_board_19_lost_communication | 2 | 555 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,3 | VT-BOARD_20_LOST_COMM | ESBMM_20_失去通信 | rack_v_t_measurement_board_20_lost_communication | 2 | 556 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,3 | VT-BOARD_21_LOST_COMM | ESBMM_21_失去通信 | rack_v_t_measurement_board_21_lost_communication | 2 | 557 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,3 | VT-BOARD_22_LOST_COMM | ESBMM_22_失去通信 | rack_v_t_measurement_board_22_lost_communication | 2 | 558 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,3 | VT-BOARD_23_LOST_COMM | ESBMM_23_失去通信 | rack_v_t_measurement_board_23_lost_communication | 2 | 559 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,3 | VT-BOARD_24_LOST_COMM | ESBMM_24_失去通信 | rack_v_t_measurement_board_24_lost_communication | 2 | 560 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,3 | VT-BOARD_25_LOST_COMM | ESBMM_25_失去通信 | rack_v_t_measurement_board_25_lost_communication | 2 | 561 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,3 | VT-BOARD_26_LOST_COMM | ESBMM_26_失去通信 | rack_v_t_measurement_board_26_lost_communication | 2 | 562 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,3 | VT-BOARD_27_LOST_COMM | ESBMM_27_失去通信 | rack_v_t_measurement_board_27_lost_communication | 2 | 563 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,3 | VT-BOARD_28_LOST_COMM | ESBMM_28_失去通信 | rack_v_t_measurement_board_28_lost_communication | 2 | 564 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,3 | VT-BOARD_29_LOST_COMM | ESBMM_29_失去通信 | rack_v_t_measurement_board_29_lost_communication | 2 | 565 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,3 | VT-BOARD_30_LOST_COMM | ESBMM_30_失去通信 | rack_v_t_measurement_board_30_lost_communication | 2 | 566 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,3 | VT-BOARD_31_LOST_COMM | ESBMM_31_失去通信 | rack_v_t_measurement_board_31_lost_communication | 2 | 567 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,3 | VT-BOARD_32_LOST_COMM | ESBMM_32_失去通信 | rack_v_t_measurement_board_32_lost_communication | 2 | 568 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,3 | VT-BOARD_33_LOST_COMM | ESBMM_33_失去通信 | rack_v_t_measurement_board_33_lost_communication | 2 | 569 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,3 | VT-BOARD_34_LOST_COMM | ESBMM_34_失去通信 | rack_v_t_measurement_board_34_lost_communication | 2 | 570 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,3 | VT-BOARD_35_LOST_COMM | ESBMM_35_失去通信 | rack_v_t_measurement_board_35_lost_communication | 2 | 571 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,3 | VT-BOARD_36_LOST_COMM | ESBMM_36_失去通信 | rack_v_t_measurement_board_36_lost_communication | 2 | 572 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,3 | VT-BOARD_37_LOST_COMM | ESBMM_37_失去通信 | rack_v_t_measurement_board_37_lost_communication | 2 | 573 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,3 | VT-BOARD_38_LOST_COMM | ESBMM_38_失去通信 | rack_v_t_measurement_board_38_lost_communication | 2 | 574 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,3 | VT-BOARD_39_LOST_COMM | ESBMM_39_失去通信 | rack_v_t_measurement_board_39_lost_communication | 2 | 575 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,3 | VT-BOARD_40_LOST_COMM | ESBMM_40_失去通信 | rack_v_t_measurement_board_40_lost_communication | 2 | 576 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,3 | TERMINAL_HIGH_TEMP_SLIGHT | 終端高溫_輕微 | rack_terminal_temperature_high_slight_alarm | 2 | 577 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,3 | TERMINAL_HIGH_TEMP_MEDIUM | 終端高溫_中度 | rack_terminal_temperature_high_medium_alarm | 2 | 578 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,3 | TERMINAL_HIGH_TEMP_SERIOUS | 終端高溫_嚴重 | rack_terminal_temperature_high_serious_alarm | 2 | 579 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,3 | MODULE_OVER_VOLT_SLIGHT | PACK過壓_輕微 | rack_module_voltage_overvoltage_slight_alarm | 2 | 580 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,3 | MODULE_OVER_VOLT_MEDIUM | PACK過壓_中度 | rack_module_voltage_overvoltage_medium_alarm | 2 | 581 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,3 | MODULE_OVER_VOLT_SERIOUS | PACK過壓_嚴重 | rack_module_voltage_overvoltage_serious_alarm | 2 | 582 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,3 | MODULE_UNDER_VOLT_SLIGHT | PACK欠壓_輕微 | rack_module_voltage_undervoltage_slight_alarm | 2 | 583 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,3 | MODULE_UNDER_VOLT_MEDIUM | PACK欠壓_中度 | rack_module_voltage_undervoltage_medium_alarm | 2 | 584 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,3 | MODULE_UNDER_VOLT_SERIOUS | PACK欠壓_嚴重 | rack_module_voltage_undervoltage_serious_alarm | 2 | 585 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,3 | CELL_VOLT_ACQ_FAULT | 電芯電壓抓取失敗 | rack_cell_voltage_acquisition_fault | 2 | 586 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,3 | CELL_TEMP_ACQ_FAULT | 電芯溫度抓取失敗 | rack_cell_temperature_acquisition_fault | 2 | 587 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,4 | RACK_LOST_COMM | 失去通訊 | rack_cbmu_lost_communication | 2 | 600 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,4 | UNDER_VOLT_SLIGHT | 欠壓_輕微 | rack_total_voltage_undervoltage_slight_alarm | 2 | 601 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,4 | UNDER_VOLT_MEDIUM | 欠壓_中度 | rack_total_voltage_undervoltage_medium_alarm | 2 | 602 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,4 | UNDER_VOLT_SERIOUS | 欠壓_嚴重 | rack_total_voltage_undervoltage_serious_alarm | 2 | 603 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,4 | OVER_VOLT_SLIGHT | 過壓_輕微 | rack_total_voltage_overvoltage_slight_alarm | 2 | 604 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,4 | OVER_VOLT_MEDIUM | 過壓_中度 | rack_total_voltage_overvoltage_medium_alarm | 2 | 605 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,4 | OVER_VOLT_SERIOUS | 過壓_嚴重 | rack_total_voltage_overvoltage_serious_alarm | 2 | 606 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,4 | OVER_CURRENT_SLIGHT | 過流_輕微 | rack_over_current_slight_alarm | 2 | 607 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,4 | OVER_CURRENT_MEDIUM | 過流_中度 | rack_over_current_medium_alarm | 2 | 608 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,4 | OVER_CURRENT_SERIOUS | 過流_嚴重 | rack_over_current_serious_alarm | 2 | 609 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,4 | CELL_UNDER_VOLT_SLIGHT | 電芯欠壓_輕微 | rack_cell_voltage_undervoltage_slight_alarm | 2 | 610 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,4 | CELL_UNDER_VOLT_MEDIUM | 電芯欠壓_中度 | rack_cell_voltage_undervoltage_medium_alarm | 2 | 611 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,4 | CELL_UNDER_VOLT_SERIOUS | 電芯欠壓_嚴重 | rack_cell_voltage_undervoltage_serious_alarm | 2 | 612 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,4 | CELL_OVER_VOLT_SLIGHT | 電芯過壓_輕微 | rack_cell_voltage_overvoltage_slight_alarm | 2 | 613 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,4 | CELL_OVER_VOLT_MEDIUM | 電芯過壓_中度 | rack_cell_voltage_overvoltage_medium_alarm | 2 | 614 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,4 | CELL_OVER_VOLT_SERIOUS | 電芯過壓_嚴重 | rack_cell_voltage_overvoltage_serious_alarm | 2 | 615 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,4 | CELL_LOW_TEMP_SLIGHT | 電芯低溫_輕微 | rack_cell_low_temperature_slight_alarm | 2 | 616 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,4 | CELL_LOW_TEMP_MEDIUM | 電芯低溫_中度 | rack_cell_low_temperature_medium_alarm | 2 | 617 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,4 | CELL_LOW_TEMP_SERIOUS | 電芯低溫_嚴重 | rack_cell_low_temperature_serious_alarm | 2 | 618 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,4 | CELL_OVER_TEMP_SLIGHT | 電芯高溫_輕微 | rack_cell_over_temperature_slight_alarm | 2 | 619 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,4 | CELL_OVER_TEMP_MEDIUM | 電芯高溫_中度 | rack_cell_over_temperature_medium_alarm | 2 | 620 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,4 | CELL_OVER_TEMP_SERIOUS | 電芯高溫_嚴重 | rack_cell_over_temperature_serious_alarm | 2 | 621 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,4 | CELL_SOC_LOW_SLIGHT | 電芯SOC過低_輕微 | rack_cell_soc_low_slight_alarm | 2 | 622 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,4 | CELL_SOC_LOW_MEDIUM | 電芯SOC過低_中度 | rack_cell_soc_low_medium_alarm | 2 | 623 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,4 | CELL_SOC_LOW_SERIOUS | 電芯SOC過低_嚴重 | rack_cell_soc_low_serious_alarm | 2 | 624 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,4 | CELL_SOC_HIGH_SLIGHT | 電芯SOC過高_輕微 | rack_cell_soc_high_slight_alarm | 2 | 625 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,4 | CELL_SOC_HIGH_MEDIUM | 電芯SOC過高_中度 | rack_cell_soc_high_medium_alarm | 2 | 626 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,4 | CELL_SOC_HIGH_SERIOUS | 電芯SOC過高_嚴重 | rack_cell_soc_high_serious_alarm | 2 | 627 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,4 | CELL_SOH_LOW_SLIGHT | 電芯SOH過低_輕微 | rack_cell_soh_low_slight_alarm | 2 | 628 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,4 | CELL_SOH_LOW_MEDIUM | 電芯SOH過低_中度 | rack_cell_soh_low_medium_alarm | 2 | 629 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,4 | CELL_SOH_LOW_SERIOUS | 電芯SOH過低_嚴重 | rack_cell_soh_low_serious_alarm | 2 | 630 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,4 | CELL_DIFF_VOLT_SLIGHT | 電芯壓差_輕微 | rack_cell_voltage_different_slight_alarm | 2 | 631 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,4 | CELL_DIFF_VOLT_MEDIUM | 電芯壓差_中度 | rack_cell_voltage_different_medium_alarm | 2 | 632 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,4 | CELL_DIFF_VOLT_SERIOUS | 電芯壓差_嚴重 | rack_cell_voltage_different_serious_alarm | 2 | 633 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,4 | CELL_DIFF_TEMP_SLIGHT | 電芯溫差_輕微 | rack_cell_temperature_different_slight_alarm | 2 | 634 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,4 | CELL_DIFF_TEMP_MEDIUM | 電芯溫差_中度 | rack_cell_temperature_different_medium_alarm | 2 | 635 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,4 | CELL_DIFF_TEMP_SERIOUS | 電芯溫差_嚴重 | rack_cell_temperature_different_serious_alarm | 2 | 636 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,4 | VT-BOARD_1_LOST_COMM | ESBMM_1_失去通信 | rack_v_t_measurement_board_1_lost_communication | 2 | 637 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,4 | VT-BOARD_2_LOST_COMM | ESBMM_2_失去通信 | rack_v_t_measurement_board_2_lost_communication | 2 | 638 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,4 | VT-BOARD_3_LOST_COMM | ESBMM_3_失去通信 | rack_v_t_measurement_board_3_lost_communication | 2 | 639 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,4 | VT-BOARD_4_LOST_COMM | ESBMM_4_失去通信 | rack_v_t_measurement_board_4_lost_communication | 2 | 640 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,4 | VT-BOARD_5_LOST_COMM | ESBMM_5_失去通信 | rack_v_t_measurement_board_5_lost_communication | 2 | 641 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,4 | VT-BOARD_6_LOST_COMM | ESBMM_6_失去通信 | rack_v_t_measurement_board_6_lost_communication | 2 | 642 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,4 | VT-BOARD_7_LOST_COMM | ESBMM_7_失去通信 | rack_v_t_measurement_board_7_lost_communication | 2 | 643 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,4 | VT-BOARD_8_LOST_COMM | ESBMM_8_失去通信 | rack_v_t_measurement_board_8_lost_communication | 2 | 644 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,4 | VT-BOARD_9_LOST_COMM | ESBMM_9_失去通信 | rack_v_t_measurement_board_9_lost_communication | 2 | 645 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,4 | VT-BOARD_10_LOST_COMM | ESBMM_10_失去通信 | rack_v_t_measurement_board_10_lost_communication | 2 | 646 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,4 | VT-BOARD_11_LOST_COMM | ESBMM_11_失去通信 | rack_v_t_measurement_board_11_lost_communication | 2 | 647 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,4 | VT-BOARD_12_LOST_COMM | ESBMM_12_失去通信 | rack_v_t_measurement_board_12_lost_communication | 2 | 648 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,4 | VT-BOARD_13_LOST_COMM | ESBMM_13_失去通信 | rack_v_t_measurement_board_13_lost_communication | 2 | 649 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,4 | VT-BOARD_14_LOST_COMM | ESBMM_14_失去通信 | rack_v_t_measurement_board_14_lost_communication | 2 | 650 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,4 | VT-BOARD_15_LOST_COMM | ESBMM_15_失去通信 | rack_v_t_measurement_board_15_lost_communication | 2 | 651 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,4 | VT-BOARD_16_LOST_COMM | ESBMM_16_失去通信 | rack_v_t_measurement_board_16_lost_communication | 2 | 652 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,4 | VT-BOARD_17_LOST_COMM | ESBMM_17_失去通信 | rack_v_t_measurement_board_17_lost_communication | 2 | 653 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,4 | VT-BOARD_18_LOST_COMM | ESBMM_18_失去通信 | rack_v_t_measurement_board_18_lost_communication | 2 | 654 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,4 | VT-BOARD_19_LOST_COMM | ESBMM_19_失去通信 | rack_v_t_measurement_board_19_lost_communication | 2 | 655 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,4 | VT-BOARD_20_LOST_COMM | ESBMM_20_失去通信 | rack_v_t_measurement_board_20_lost_communication | 2 | 656 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,4 | VT-BOARD_21_LOST_COMM | ESBMM_21_失去通信 | rack_v_t_measurement_board_21_lost_communication | 2 | 657 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,4 | VT-BOARD_22_LOST_COMM | ESBMM_22_失去通信 | rack_v_t_measurement_board_22_lost_communication | 2 | 658 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,4 | VT-BOARD_23_LOST_COMM | ESBMM_23_失去通信 | rack_v_t_measurement_board_23_lost_communication | 2 | 659 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,4 | VT-BOARD_24_LOST_COMM | ESBMM_24_失去通信 | rack_v_t_measurement_board_24_lost_communication | 2 | 660 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,4 | VT-BOARD_25_LOST_COMM | ESBMM_25_失去通信 | rack_v_t_measurement_board_25_lost_communication | 2 | 661 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,4 | VT-BOARD_26_LOST_COMM | ESBMM_26_失去通信 | rack_v_t_measurement_board_26_lost_communication | 2 | 662 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,4 | VT-BOARD_27_LOST_COMM | ESBMM_27_失去通信 | rack_v_t_measurement_board_27_lost_communication | 2 | 663 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,4 | VT-BOARD_28_LOST_COMM | ESBMM_28_失去通信 | rack_v_t_measurement_board_28_lost_communication | 2 | 664 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,4 | VT-BOARD_29_LOST_COMM | ESBMM_29_失去通信 | rack_v_t_measurement_board_29_lost_communication | 2 | 665 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,4 | VT-BOARD_30_LOST_COMM | ESBMM_30_失去通信 | rack_v_t_measurement_board_30_lost_communication | 2 | 666 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,4 | VT-BOARD_31_LOST_COMM | ESBMM_31_失去通信 | rack_v_t_measurement_board_31_lost_communication | 2 | 667 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,4 | VT-BOARD_32_LOST_COMM | ESBMM_32_失去通信 | rack_v_t_measurement_board_32_lost_communication | 2 | 668 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,4 | VT-BOARD_33_LOST_COMM | ESBMM_33_失去通信 | rack_v_t_measurement_board_33_lost_communication | 2 | 669 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,4 | VT-BOARD_34_LOST_COMM | ESBMM_34_失去通信 | rack_v_t_measurement_board_34_lost_communication | 2 | 670 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,4 | VT-BOARD_35_LOST_COMM | ESBMM_35_失去通信 | rack_v_t_measurement_board_35_lost_communication | 2 | 671 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,4 | VT-BOARD_36_LOST_COMM | ESBMM_36_失去通信 | rack_v_t_measurement_board_36_lost_communication | 2 | 672 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,4 | VT-BOARD_37_LOST_COMM | ESBMM_37_失去通信 | rack_v_t_measurement_board_37_lost_communication | 2 | 673 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,4 | VT-BOARD_38_LOST_COMM | ESBMM_38_失去通信 | rack_v_t_measurement_board_38_lost_communication | 2 | 674 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,4 | VT-BOARD_39_LOST_COMM | ESBMM_39_失去通信 | rack_v_t_measurement_board_39_lost_communication | 2 | 675 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,4 | VT-BOARD_40_LOST_COMM | ESBMM_40_失去通信 | rack_v_t_measurement_board_40_lost_communication | 2 | 676 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,4 | TERMINAL_HIGH_TEMP_SLIGHT | 終端高溫_輕微 | rack_terminal_temperature_high_slight_alarm | 2 | 677 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,4 | TERMINAL_HIGH_TEMP_MEDIUM | 終端高溫_中度 | rack_terminal_temperature_high_medium_alarm | 2 | 678 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,4 | TERMINAL_HIGH_TEMP_SERIOUS | 終端高溫_嚴重 | rack_terminal_temperature_high_serious_alarm | 2 | 679 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,4 | MODULE_OVER_VOLT_SLIGHT | PACK過壓_輕微 | rack_module_voltage_overvoltage_slight_alarm | 2 | 680 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,4 | MODULE_OVER_VOLT_MEDIUM | PACK過壓_中度 | rack_module_voltage_overvoltage_medium_alarm | 2 | 681 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,4 | MODULE_OVER_VOLT_SERIOUS | PACK過壓_嚴重 | rack_module_voltage_overvoltage_serious_alarm | 2 | 682 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,4 | MODULE_UNDER_VOLT_SLIGHT | PACK欠壓_輕微 | rack_module_voltage_undervoltage_slight_alarm | 2 | 683 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,4 | MODULE_UNDER_VOLT_MEDIUM | PACK欠壓_中度 | rack_module_voltage_undervoltage_medium_alarm | 2 | 684 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,4 | MODULE_UNDER_VOLT_SERIOUS | PACK欠壓_嚴重 | rack_module_voltage_undervoltage_serious_alarm | 2 | 685 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,4 | CELL_VOLT_ACQ_FAULT | 電芯電壓抓取失敗 | rack_cell_voltage_acquisition_fault | 2 | 686 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,4 | CELL_TEMP_ACQ_FAULT | 電芯溫度抓取失敗 | rack_cell_temperature_acquisition_fault | 2 | 687 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,5 | RACK_LOST_COMM | 失去通訊 | rack_cbmu_lost_communication | 2 | 700 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,5 | UNDER_VOLT_SLIGHT | 欠壓_輕微 | rack_total_voltage_undervoltage_slight_alarm | 2 | 701 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,5 | UNDER_VOLT_MEDIUM | 欠壓_中度 | rack_total_voltage_undervoltage_medium_alarm | 2 | 702 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,5 | UNDER_VOLT_SERIOUS | 欠壓_嚴重 | rack_total_voltage_undervoltage_serious_alarm | 2 | 703 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,5 | OVER_VOLT_SLIGHT | 過壓_輕微 | rack_total_voltage_overvoltage_slight_alarm | 2 | 704 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,5 | OVER_VOLT_MEDIUM | 過壓_中度 | rack_total_voltage_overvoltage_medium_alarm | 2 | 705 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,5 | OVER_VOLT_SERIOUS | 過壓_嚴重 | rack_total_voltage_overvoltage_serious_alarm | 2 | 706 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,5 | OVER_CURRENT_SLIGHT | 過流_輕微 | rack_over_current_slight_alarm | 2 | 707 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,5 | OVER_CURRENT_MEDIUM | 過流_中度 | rack_over_current_medium_alarm | 2 | 708 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,5 | OVER_CURRENT_SERIOUS | 過流_嚴重 | rack_over_current_serious_alarm | 2 | 709 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,5 | CELL_UNDER_VOLT_SLIGHT | 電芯欠壓_輕微 | rack_cell_voltage_undervoltage_slight_alarm | 2 | 710 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,5 | CELL_UNDER_VOLT_MEDIUM | 電芯欠壓_中度 | rack_cell_voltage_undervoltage_medium_alarm | 2 | 711 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,5 | CELL_UNDER_VOLT_SERIOUS | 電芯欠壓_嚴重 | rack_cell_voltage_undervoltage_serious_alarm | 2 | 712 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,5 | CELL_OVER_VOLT_SLIGHT | 電芯過壓_輕微 | rack_cell_voltage_overvoltage_slight_alarm | 2 | 713 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,5 | CELL_OVER_VOLT_MEDIUM | 電芯過壓_中度 | rack_cell_voltage_overvoltage_medium_alarm | 2 | 714 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,5 | CELL_OVER_VOLT_SERIOUS | 電芯過壓_嚴重 | rack_cell_voltage_overvoltage_serious_alarm | 2 | 715 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,5 | CELL_LOW_TEMP_SLIGHT | 電芯低溫_輕微 | rack_cell_low_temperature_slight_alarm | 2 | 716 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,5 | CELL_LOW_TEMP_MEDIUM | 電芯低溫_中度 | rack_cell_low_temperature_medium_alarm | 2 | 717 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,5 | CELL_LOW_TEMP_SERIOUS | 電芯低溫_嚴重 | rack_cell_low_temperature_serious_alarm | 2 | 718 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,5 | CELL_OVER_TEMP_SLIGHT | 電芯高溫_輕微 | rack_cell_over_temperature_slight_alarm | 2 | 719 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,5 | CELL_OVER_TEMP_MEDIUM | 電芯高溫_中度 | rack_cell_over_temperature_medium_alarm | 2 | 720 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,5 | CELL_OVER_TEMP_SERIOUS | 電芯高溫_嚴重 | rack_cell_over_temperature_serious_alarm | 2 | 721 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,5 | CELL_SOC_LOW_SLIGHT | 電芯SOC過低_輕微 | rack_cell_soc_low_slight_alarm | 2 | 722 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,5 | CELL_SOC_LOW_MEDIUM | 電芯SOC過低_中度 | rack_cell_soc_low_medium_alarm | 2 | 723 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,5 | CELL_SOC_LOW_SERIOUS | 電芯SOC過低_嚴重 | rack_cell_soc_low_serious_alarm | 2 | 724 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,5 | CELL_SOC_HIGH_SLIGHT | 電芯SOC過高_輕微 | rack_cell_soc_high_slight_alarm | 2 | 725 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,5 | CELL_SOC_HIGH_MEDIUM | 電芯SOC過高_中度 | rack_cell_soc_high_medium_alarm | 2 | 726 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,5 | CELL_SOC_HIGH_SERIOUS | 電芯SOC過高_嚴重 | rack_cell_soc_high_serious_alarm | 2 | 727 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,5 | CELL_SOH_LOW_SLIGHT | 電芯SOH過低_輕微 | rack_cell_soh_low_slight_alarm | 2 | 728 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,5 | CELL_SOH_LOW_MEDIUM | 電芯SOH過低_中度 | rack_cell_soh_low_medium_alarm | 2 | 729 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,5 | CELL_SOH_LOW_SERIOUS | 電芯SOH過低_嚴重 | rack_cell_soh_low_serious_alarm | 2 | 730 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,5 | CELL_DIFF_VOLT_SLIGHT | 電芯壓差_輕微 | rack_cell_voltage_different_slight_alarm | 2 | 731 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,5 | CELL_DIFF_VOLT_MEDIUM | 電芯壓差_中度 | rack_cell_voltage_different_medium_alarm | 2 | 732 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,5 | CELL_DIFF_VOLT_SERIOUS | 電芯壓差_嚴重 | rack_cell_voltage_different_serious_alarm | 2 | 733 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,5 | CELL_DIFF_TEMP_SLIGHT | 電芯溫差_輕微 | rack_cell_temperature_different_slight_alarm | 2 | 734 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,5 | CELL_DIFF_TEMP_MEDIUM | 電芯溫差_中度 | rack_cell_temperature_different_medium_alarm | 2 | 735 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,5 | CELL_DIFF_TEMP_SERIOUS | 電芯溫差_嚴重 | rack_cell_temperature_different_serious_alarm | 2 | 736 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,5 | VT-BOARD_1_LOST_COMM | ESBMM_1_失去通信 | rack_v_t_measurement_board_1_lost_communication | 2 | 737 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,5 | VT-BOARD_2_LOST_COMM | ESBMM_2_失去通信 | rack_v_t_measurement_board_2_lost_communication | 2 | 738 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,5 | VT-BOARD_3_LOST_COMM | ESBMM_3_失去通信 | rack_v_t_measurement_board_3_lost_communication | 2 | 739 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,5 | VT-BOARD_4_LOST_COMM | ESBMM_4_失去通信 | rack_v_t_measurement_board_4_lost_communication | 2 | 740 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,5 | VT-BOARD_5_LOST_COMM | ESBMM_5_失去通信 | rack_v_t_measurement_board_5_lost_communication | 2 | 741 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,5 | VT-BOARD_6_LOST_COMM | ESBMM_6_失去通信 | rack_v_t_measurement_board_6_lost_communication | 2 | 742 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,5 | VT-BOARD_7_LOST_COMM | ESBMM_7_失去通信 | rack_v_t_measurement_board_7_lost_communication | 2 | 743 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,5 | VT-BOARD_8_LOST_COMM | ESBMM_8_失去通信 | rack_v_t_measurement_board_8_lost_communication | 2 | 744 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,5 | VT-BOARD_9_LOST_COMM | ESBMM_9_失去通信 | rack_v_t_measurement_board_9_lost_communication | 2 | 745 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,5 | VT-BOARD_10_LOST_COMM | ESBMM_10_失去通信 | rack_v_t_measurement_board_10_lost_communication | 2 | 746 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,5 | VT-BOARD_11_LOST_COMM | ESBMM_11_失去通信 | rack_v_t_measurement_board_11_lost_communication | 2 | 747 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,5 | VT-BOARD_12_LOST_COMM | ESBMM_12_失去通信 | rack_v_t_measurement_board_12_lost_communication | 2 | 748 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,5 | VT-BOARD_13_LOST_COMM | ESBMM_13_失去通信 | rack_v_t_measurement_board_13_lost_communication | 2 | 749 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,5 | VT-BOARD_14_LOST_COMM | ESBMM_14_失去通信 | rack_v_t_measurement_board_14_lost_communication | 2 | 750 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,5 | VT-BOARD_15_LOST_COMM | ESBMM_15_失去通信 | rack_v_t_measurement_board_15_lost_communication | 2 | 751 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,5 | VT-BOARD_16_LOST_COMM | ESBMM_16_失去通信 | rack_v_t_measurement_board_16_lost_communication | 2 | 752 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,5 | VT-BOARD_17_LOST_COMM | ESBMM_17_失去通信 | rack_v_t_measurement_board_17_lost_communication | 2 | 753 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,5 | VT-BOARD_18_LOST_COMM | ESBMM_18_失去通信 | rack_v_t_measurement_board_18_lost_communication | 2 | 754 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,5 | VT-BOARD_19_LOST_COMM | ESBMM_19_失去通信 | rack_v_t_measurement_board_19_lost_communication | 2 | 755 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,5 | VT-BOARD_20_LOST_COMM | ESBMM_20_失去通信 | rack_v_t_measurement_board_20_lost_communication | 2 | 756 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,5 | VT-BOARD_21_LOST_COMM | ESBMM_21_失去通信 | rack_v_t_measurement_board_21_lost_communication | 2 | 757 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,5 | VT-BOARD_22_LOST_COMM | ESBMM_22_失去通信 | rack_v_t_measurement_board_22_lost_communication | 2 | 758 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,5 | VT-BOARD_23_LOST_COMM | ESBMM_23_失去通信 | rack_v_t_measurement_board_23_lost_communication | 2 | 759 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,5 | VT-BOARD_24_LOST_COMM | ESBMM_24_失去通信 | rack_v_t_measurement_board_24_lost_communication | 2 | 760 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,5 | VT-BOARD_25_LOST_COMM | ESBMM_25_失去通信 | rack_v_t_measurement_board_25_lost_communication | 2 | 761 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,5 | VT-BOARD_26_LOST_COMM | ESBMM_26_失去通信 | rack_v_t_measurement_board_26_lost_communication | 2 | 762 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,5 | VT-BOARD_27_LOST_COMM | ESBMM_27_失去通信 | rack_v_t_measurement_board_27_lost_communication | 2 | 763 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,5 | VT-BOARD_28_LOST_COMM | ESBMM_28_失去通信 | rack_v_t_measurement_board_28_lost_communication | 2 | 764 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,5 | VT-BOARD_29_LOST_COMM | ESBMM_29_失去通信 | rack_v_t_measurement_board_29_lost_communication | 2 | 765 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,5 | VT-BOARD_30_LOST_COMM | ESBMM_30_失去通信 | rack_v_t_measurement_board_30_lost_communication | 2 | 766 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,5 | VT-BOARD_31_LOST_COMM | ESBMM_31_失去通信 | rack_v_t_measurement_board_31_lost_communication | 2 | 767 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,5 | VT-BOARD_32_LOST_COMM | ESBMM_32_失去通信 | rack_v_t_measurement_board_32_lost_communication | 2 | 768 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,5 | VT-BOARD_33_LOST_COMM | ESBMM_33_失去通信 | rack_v_t_measurement_board_33_lost_communication | 2 | 769 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,5 | VT-BOARD_34_LOST_COMM | ESBMM_34_失去通信 | rack_v_t_measurement_board_34_lost_communication | 2 | 770 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,5 | VT-BOARD_35_LOST_COMM | ESBMM_35_失去通信 | rack_v_t_measurement_board_35_lost_communication | 2 | 771 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,5 | VT-BOARD_36_LOST_COMM | ESBMM_36_失去通信 | rack_v_t_measurement_board_36_lost_communication | 2 | 772 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,5 | VT-BOARD_37_LOST_COMM | ESBMM_37_失去通信 | rack_v_t_measurement_board_37_lost_communication | 2 | 773 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,5 | VT-BOARD_38_LOST_COMM | ESBMM_38_失去通信 | rack_v_t_measurement_board_38_lost_communication | 2 | 774 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,5 | VT-BOARD_39_LOST_COMM | ESBMM_39_失去通信 | rack_v_t_measurement_board_39_lost_communication | 2 | 775 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,5 | VT-BOARD_40_LOST_COMM | ESBMM_40_失去通信 | rack_v_t_measurement_board_40_lost_communication | 2 | 776 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,5 | TERMINAL_HIGH_TEMP_SLIGHT | 終端高溫_輕微 | rack_terminal_temperature_high_slight_alarm | 2 | 777 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,5 | TERMINAL_HIGH_TEMP_MEDIUM | 終端高溫_中度 | rack_terminal_temperature_high_medium_alarm | 2 | 778 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,5 | TERMINAL_HIGH_TEMP_SERIOUS | 終端高溫_嚴重 | rack_terminal_temperature_high_serious_alarm | 2 | 779 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,5 | MODULE_OVER_VOLT_SLIGHT | PACK過壓_輕微 | rack_module_voltage_overvoltage_slight_alarm | 2 | 780 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,5 | MODULE_OVER_VOLT_MEDIUM | PACK過壓_中度 | rack_module_voltage_overvoltage_medium_alarm | 2 | 781 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,5 | MODULE_OVER_VOLT_SERIOUS | PACK過壓_嚴重 | rack_module_voltage_overvoltage_serious_alarm | 2 | 782 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,5 | MODULE_UNDER_VOLT_SLIGHT | PACK欠壓_輕微 | rack_module_voltage_undervoltage_slight_alarm | 2 | 783 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 0 |  | 1 | false
individual | 1 | rack_list,5 | MODULE_UNDER_VOLT_MEDIUM | PACK欠壓_中度 | rack_module_voltage_undervoltage_medium_alarm | 2 | 784 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,5 | MODULE_UNDER_VOLT_SERIOUS | PACK欠壓_嚴重 | rack_module_voltage_undervoltage_serious_alarm | 2 | 785 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 | rack_list,5 | CELL_VOLT_ACQ_FAULT | 電芯電壓抓取失敗 | rack_cell_voltage_acquisition_fault | 2 | 786 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 | rack_list,5 | CELL_TEMP_ACQ_FAULT | 電芯溫度抓取失敗 | rack_cell_temperature_acquisition_fault | 2 | 787 |  | Int | 1 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 |  |  |  | breaker_code | 4 | 1 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  |  | breaker_status | 4 | 1 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "opening" }, { "input": "1", "output": "closing" } ] | false | 0 |  | 1 | false
individual | 1 |  |  |  | voltage | 4 | 2 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | current | 4 | 3 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | -3200.0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | soc | 4 | 4 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | soh | 4 | 5 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | max_cell_voltage | 4 | 6 |  | Double | 16 | Unsigned | Big Endian | 0.001 | 3 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | max_cell_volt_rack_address | 4 | 7 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | max_cell_volt_point_address | 4 | 8 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | min_cell_voltage | 4 | 9 |  | Double | 16 | Unsigned | Big Endian | 0.001 | 3 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | min_cell_volt_rack_address | 4 | 10 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | min_cell_volt_point_address | 4 | 11 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | max_cell_temperature | 4 | 12 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | -40 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | max_cell_temp_rack_address | 4 | 13 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | max_cell_temp_point_address | 4 | 14 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | min_cell_temperature | 4 | 15 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | -40 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | min_cell_temp_rack_address | 4 | 16 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | min_cell_temp_point_address | 4 | 17 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | total_charge_capacity | 4 | 18 |  | Double | 32 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | total_discharge_capacity | 4 | 20 |  | Double | 32 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | system_accumulated_charge_quantity_for_a_single_time | 4 | 22 |  | Double | 32 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | system_accumulated_discharge_quantity_for_a_single_time | 4 | 24 |  | Double | 32 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | allow_charge_capacity | 4 | 26 |  | Double | 32 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | allow_discharge_capacity | 4 | 28 |  | Double | 32 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | available_discharge_time | 4 | 30 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | available_charging_time | 4 | 31 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | allow_discharge_max_power | 4 | 32 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | allow_charge_max_power | 4 | 33 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | allow_discharge_max_current | 4 | 34 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | allow_charge_max_current | 4 | 35 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | discharge_times_of_the_day | 4 | 36 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | charge_times_of_the_day | 4 | 37 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | daily_discharging_capacity | 4 | 38 |  | Double | 32 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | daily_charging_capacity | 4 | 40 |  | Double | 32 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | operating_temperature | 4 | 42 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | -40 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | status | 4 | 43 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "初始化" }, { "input": "1", "output": "充電" }, { "input": "2", "output": "放電" }, { "input": "3", "output": "就緒" }, { "input": "4", "output": "群集維護" }, { "input": "5", "output": "禁止充電" }, { "input": "6", "output": "禁止放電" }, { "input": "7", "output": "禁止充放電" }, { "input": "8", "output": "故障" }, { "input": "9", "output": "故障恢復" }, { "input": "10", "output": "測試模式" }, { "input": "11", "output": "關機" }, { "input": "12", "output": "關機完成" } ] | false | 0 |  | 1 | false
individual | 1 |  |  |  | bms_charge_and_discharge_state | 4 | 44 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "Others" }, { "input": "1", "output": "Discharge" }, { "input": "2", "output": "Charge" } ] | false | 0 |  | 1 | false
individual | 1 |  |  |  | insulation_resistance | 4 | 45 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | pcs_and_bms_communication_fault | 4 | 46 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 |  |  |  | ems_and_bms_communication_fault | 4 | 47 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 |  |  |  | cycle | 4 | 48 |  | Int | 32 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | equivalent_cycle | 4 | 50 |  | Int | 32 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 | rack_list,0 |  |  | rack_state | 4 | 100 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "初始化" }, { "input": "1", "output": "充電" }, { "input": "2", "output": "放電" }, { "input": "3", "output": "就緒" }, { "input": "4", "output": "群集維護" }, { "input": "5", "output": "禁止充電" }, { "input": "6", "output": "禁止放電" }, { "input": "7", "output": "禁止充放電" }, { "input": "8", "output": "故障" }, { "input": "9", "output": "故障恢復" }, { "input": "10", "output": "測試模式" } ] | false | 0 |  | 1 | false
individual | 1 | rack_list,0 |  |  | allow_charge_max_power | 4 | 101 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 | rack_list,0 |  |  | allow_discharge_max_power | 4 | 102 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 | rack_list,0 |  |  | allow_charge_max_volt | 4 | 103 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 | rack_list,0 |  |  | allow_discharge_max_volt | 4 | 104 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 | rack_list,0 |  |  | allow_charge_max_current | 4 | 105 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 | rack_list,0 |  |  | allow_discharge_max_current | 4 | 106 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 | rack_list,0 |  |  | rack_input_1 | 4 | 107 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "Off" }, { "input": "1", "output": "On" } ] | false | 0 |  | 1 | false
individual | 1 | rack_list,0 |  |  | rack_input_2 | 4 | 108 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "Off" }, { "input": "1", "output": "On" } ] | false | 0 |  | 1 | false
individual | 1 | rack_list,0 |  |  | rack_input_3 | 4 | 109 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "Off" }, { "input": "1", "output": "On" } ] | false | 0 |  | 1 | false
individual | 1 | rack_list,0 |  |  | rack_input_4 | 4 | 110 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "Off" }, { "input": "1", "output": "On" } ] | false | 0 |  | 1 | false
individual | 1 | rack_list,0 |  |  | rack_input_5 | 4 | 111 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "Off" }, { "input": "1", "output": "On" } ] | false | 0 |  | 1 | false
individual | 1 | rack_list,0 |  |  | rack_input_6 | 4 | 112 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "Off" }, { "input": "1", "output": "On" } ] | false | 0 |  | 1 | false
individual | 1 | rack_list,0 |  |  | rack_input_7 | 4 | 113 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "Off" }, { "input": "1", "output": "On" } ] | false | 0 |  | 1 | false
individual | 1 | rack_list,0 |  |  | rack_input_8 | 4 | 114 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "Off" }, { "input": "1", "output": "On" } ] | false | 0 |  | 1 | false
individual | 1 | rack_list,0 |  |  | voltage | 4 | 115 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 | rack_list,0 |  |  | current | 4 | 116 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | -3200 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 | rack_list,0 |  |  | temperature | 4 | 117 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | -40 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 | rack_list,0 |  |  | soc | 4 | 118 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 | rack_list,0 |  |  | soh | 4 | 119 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 | rack_list,0 |  |  | insulation_resistance | 4 | 120 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 | rack_list,0 |  |  | cell_avg_voltage | 4 | 121 |  | Double | 16 | Unsigned | Big Endian | 0.001 | 3 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 | rack_list,0 |  |  | cell_avg_temperature | 4 | 122 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | -40 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 | rack_list,0 |  |  | max_cell_voltage | 4 | 123 |  | Double | 16 | Unsigned | Big Endian | 0.001 | 3 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 | rack_list,0 |  |  | max_cell_volt_point_address | 4 | 124 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 | rack_list,0 |  |  | min_cell_voltage | 4 | 125 |  | Double | 16 | Unsigned | Big Endian | 0.001 | 3 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 | rack_list,0 |  |  | min_cell_volt_point_address | 4 | 126 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 | rack_list,0 |  |  | max_cell_temperature | 4 | 127 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | -40 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 | rack_list,0 |  |  | max_cell_temp_point_address | 4 | 128 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 | rack_list,0 |  |  | min_cell_temperature | 4 | 129 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | -40 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 | rack_list,0 |  |  | min_cell_temp_point_address | 4 | 130 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 | rack_list,0 |  |  | max_cell_soc | 4 | 131 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 | rack_list,0 |  |  | max_cell_soc_point_address | 4 | 132 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 | rack_list,0 |  |  | min_cell_soc | 4 | 133 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 | rack_list,0 |  |  | min_cell_soc_point_address | 4 | 134 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 | rack_list,0 |  |  | max_cell_soh | 4 | 135 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 | rack_list,0 |  |  | max_cell_soh_point_address | 4 | 136 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 | rack_list,0 |  |  | min_cell_soh | 4 | 137 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 | rack_list,0 |  |  | min_cell_soh_point_address | 4 | 138 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 | rack_list,0 |  |  | total_charge_capacity | 4 | 139 |  | Double | 32 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 | rack_list,0 |  |  | total_discharge_capacity | 4 | 141 |  | Double | 32 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 | rack_list,0 |  |  | rack_accumulated_charge_quantity_for_a_single_time | 4 | 143 |  | Double | 32 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 | rack_list,0 |  |  | rack_accumulated_discharge_quantity_for_a_single_time | 4 | 145 |  | Double | 32 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 | rack_list,0 |  |  | allow_charge_capacity | 4 | 147 |  | Double | 32 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 | rack_list,0 |  |  | allow_discharge_capacity | 4 | 149 |  | Double | 32 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 0 |  | 1 | false
array | 1 | rack_list,0 |  |  | module_soc | 4 |  |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 | 151 | 8 | false
array | 1 | rack_list,0 |  |  | cell_volt | 4 |  |  | Double | 16 | Unsigned | Big Endian | 0.001 | 3 | 0 | false |  | false |  | false | 0 | 191 | 416 | false
array | 1 | rack_list,0 |  |  | cell_temp | 4 |  |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | -40 | false |  | false |  | false | 0 | 891 | 416 | false
array | 1 | rack_list,0 |  |  | cell_soc | 4 |  |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 | 1591 | 416 | false
array | 1 | rack_list,0 |  |  | cell_soh | 4 |  |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 | 2291 | 416 | false
array | 1 | rack_list,0 |  |  | cell_terminal_temp | 4 |  |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | -40 | false |  | false |  | false | 1 | 2991 | 100 | false
individual | 1 | rack_list,1 |  |  | rack_state | 4 | 3100 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "初始化" }, { "input": "1", "output": "充電" }, { "input": "2", "output": "放電" }, { "input": "3", "output": "就緒" }, { "input": "4", "output": "群集維護" }, { "input": "5", "output": "禁止充電" }, { "input": "6", "output": "禁止放電" }, { "input": "7", "output": "禁止充放電" }, { "input": "8", "output": "故障" }, { "input": "9", "output": "故障恢復" }, { "input": "10", "output": "測試模式" } ] | false | 1 |  | 1 | false
individual | 1 | rack_list,1 |  |  | allow_charge_max_power | 4 | 3101 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,1 |  |  | allow_discharge_max_power | 4 | 3102 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,1 |  |  | allow_charge_max_volt | 4 | 3103 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,1 |  |  | allow_discharge_max_volt | 4 | 3104 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,1 |  |  | allow_charge_max_current | 4 | 3105 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,1 |  |  | allow_discharge_max_current | 4 | 3106 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,1 |  |  | rack_input_1 | 4 | 3107 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "Off" }, { "input": "1", "output": "On" } ] | false | 1 |  | 1 | false
individual | 1 | rack_list,1 |  |  | rack_input_2 | 4 | 3108 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "Off" }, { "input": "1", "output": "On" } ] | false | 1 |  | 1 | false
individual | 1 | rack_list,1 |  |  | rack_input_3 | 4 | 3109 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "Off" }, { "input": "1", "output": "On" } ] | false | 1 |  | 1 | false
individual | 1 | rack_list,1 |  |  | rack_input_4 | 4 | 3110 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "Off" }, { "input": "1", "output": "On" } ] | false | 1 |  | 1 | false
individual | 1 | rack_list,1 |  |  | rack_input_5 | 4 | 3111 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "Off" }, { "input": "1", "output": "On" } ] | false | 1 |  | 1 | false
individual | 1 | rack_list,1 |  |  | rack_input_6 | 4 | 3112 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "Off" }, { "input": "1", "output": "On" } ] | false | 1 |  | 1 | false
individual | 1 | rack_list,1 |  |  | rack_input_7 | 4 | 3113 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "Off" }, { "input": "1", "output": "On" } ] | false | 1 |  | 1 | false
individual | 1 | rack_list,1 |  |  | rack_input_8 | 4 | 3114 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "Off" }, { "input": "1", "output": "On" } ] | false | 1 |  | 1 | false
individual | 1 | rack_list,1 |  |  | voltage | 4 | 3115 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,1 |  |  | current | 4 | 3116 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | -3200 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,1 |  |  | temperature | 4 | 3117 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | -40 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,1 |  |  | soc | 4 | 3118 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,1 |  |  | soh | 4 | 3119 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,1 |  |  | insulation_resistance | 4 | 3120 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,1 |  |  | cell_avg_voltage | 4 | 3121 |  | Double | 16 | Unsigned | Big Endian | 0.001 | 3 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,1 |  |  | cell_avg_temperature | 4 | 3122 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | -40 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,1 |  |  | max_cell_voltage | 4 | 3123 |  | Double | 16 | Unsigned | Big Endian | 0.001 | 3 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,1 |  |  | max_cell_volt_point_address | 4 | 3124 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,1 |  |  | min_cell_voltage | 4 | 3125 |  | Double | 16 | Unsigned | Big Endian | 0.001 | 3 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,1 |  |  | min_cell_volt_point_address | 4 | 3126 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,1 |  |  | max_cell_temperature | 4 | 3127 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | -40 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,1 |  |  | max_cell_temp_point_address | 4 | 3128 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,1 |  |  | min_cell_temperature | 4 | 3129 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | -40 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,1 |  |  | min_cell_temp_point_address | 4 | 3130 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,1 |  |  | max_cell_soc | 4 | 3131 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,1 |  |  | max_cell_soc_point_address | 4 | 3132 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,1 |  |  | min_cell_soc | 4 | 3133 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,1 |  |  | min_cell_soc_point_address | 4 | 3134 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,1 |  |  | max_cell_soh | 4 | 3135 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,1 |  |  | max_cell_soh_point_address | 4 | 3136 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,1 |  |  | min_cell_soh | 4 | 3137 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,1 |  |  | min_cell_soh_point_address | 4 | 3138 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,1 |  |  | total_charge_capacity | 4 | 3139 |  | Double | 32 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,1 |  |  | total_discharge_capacity | 4 | 3141 |  | Double | 32 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,1 |  |  | rack_accumulated_charge_quantity_for_a_single_time | 4 | 3143 |  | Double | 32 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,1 |  |  | rack_accumulated_discharge_quantity_for_a_single_time | 4 | 3145 |  | Double | 32 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,1 |  |  | allow_charge_capacity | 4 | 3147 |  | Double | 32 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,1 |  |  | allow_discharge_capacity | 4 | 3149 |  | Double | 32 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
array | 1 | rack_list,1 |  |  | module_soc | 4 |  |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 | 3151 | 8 | false
array | 1 | rack_list,1 |  |  | cell_volt | 4 |  |  | Double | 16 | Unsigned | Big Endian | 0.001 | 3 | 0 | false |  | false |  | false | 0 | 3191 | 416 | false
array | 1 | rack_list,1 |  |  | cell_temp | 4 |  |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | -40 | false |  | false |  | false | 0 | 3891 | 416 | false
array | 1 | rack_list,1 |  |  | cell_soc | 4 |  |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 | 4591 | 416 | false
array | 1 | rack_list,1 |  |  | cell_soh | 4 |  |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 | 5291 | 416 | false
array | 1 | rack_list,1 |  |  | cell_terminal_temp | 4 |  |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | -40 | false |  | false |  | false | 1 | 5991 | 100 | false
individual | 1 | rack_list,2 |  |  | rack_state | 4 | 6100 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "初始化" }, { "input": "1", "output": "充電" }, { "input": "2", "output": "放電" }, { "input": "3", "output": "就緒" }, { "input": "4", "output": "群集維護" }, { "input": "5", "output": "禁止充電" }, { "input": "6", "output": "禁止放電" }, { "input": "7", "output": "禁止充放電" }, { "input": "8", "output": "故障" }, { "input": "9", "output": "故障恢復" }, { "input": "10", "output": "測試模式" } ] | false | 1 |  | 1 | false
individual | 1 | rack_list,2 |  |  | allow_charge_max_power | 4 | 6101 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,2 |  |  | allow_discharge_max_power | 4 | 6102 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,2 |  |  | allow_charge_max_volt | 4 | 6103 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,2 |  |  | allow_discharge_max_volt | 4 | 6104 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,2 |  |  | allow_charge_max_current | 4 | 6105 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,2 |  |  | allow_discharge_max_current | 4 | 6106 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,2 |  |  | rack_input_1 | 4 | 6107 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "Off" }, { "input": "1", "output": "On" } ] | false | 1 |  | 1 | false
individual | 1 | rack_list,2 |  |  | rack_input_2 | 4 | 6108 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "Off" }, { "input": "1", "output": "On" } ] | false | 1 |  | 1 | false
individual | 1 | rack_list,2 |  |  | rack_input_3 | 4 | 6109 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "Off" }, { "input": "1", "output": "On" } ] | false | 1 |  | 1 | false
individual | 1 | rack_list,2 |  |  | rack_input_4 | 4 | 6110 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "Off" }, { "input": "1", "output": "On" } ] | false | 1 |  | 1 | false
individual | 1 | rack_list,2 |  |  | rack_input_5 | 4 | 6111 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "Off" }, { "input": "1", "output": "On" } ] | false | 1 |  | 1 | false
individual | 1 | rack_list,2 |  |  | rack_input_6 | 4 | 6112 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "Off" }, { "input": "1", "output": "On" } ] | false | 1 |  | 1 | false
individual | 1 | rack_list,2 |  |  | rack_input_7 | 4 | 6113 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "Off" }, { "input": "1", "output": "On" } ] | false | 1 |  | 1 | false
individual | 1 | rack_list,2 |  |  | rack_input_8 | 4 | 6114 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "Off" }, { "input": "1", "output": "On" } ] | false | 1 |  | 1 | false
individual | 1 | rack_list,2 |  |  | voltage | 4 | 6115 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,2 |  |  | current | 4 | 6116 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | -3200 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,2 |  |  | temperature | 4 | 6117 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | -40 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,2 |  |  | soc | 4 | 6118 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,2 |  |  | soh | 4 | 6119 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,2 |  |  | insulation_resistance | 4 | 6120 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,2 |  |  | cell_avg_voltage | 4 | 6121 |  | Double | 16 | Unsigned | Big Endian | 0.001 | 3 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,2 |  |  | cell_avg_temperature | 4 | 6122 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | -40 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,2 |  |  | max_cell_voltage | 4 | 6123 |  | Double | 16 | Unsigned | Big Endian | 0.001 | 3 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,2 |  |  | max_cell_volt_point_address | 4 | 6124 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,2 |  |  | min_cell_voltage | 4 | 6125 |  | Double | 16 | Unsigned | Big Endian | 0.001 | 3 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,2 |  |  | min_cell_volt_point_address | 4 | 6126 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,2 |  |  | max_cell_temperature | 4 | 6127 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | -40 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,2 |  |  | max_cell_temp_point_address | 4 | 6128 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,2 |  |  | min_cell_temperature | 4 | 6129 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | -40 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,2 |  |  | min_cell_temp_point_address | 4 | 6130 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,2 |  |  | max_cell_soc | 4 | 6131 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,2 |  |  | max_cell_soc_point_address | 4 | 6132 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,2 |  |  | min_cell_soc | 4 | 6133 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,2 |  |  | min_cell_soc_point_address | 4 | 6134 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,2 |  |  | max_cell_soh | 4 | 6135 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,2 |  |  | max_cell_soh_point_address | 4 | 6136 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,2 |  |  | min_cell_soh | 4 | 6137 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,2 |  |  | min_cell_soh_point_address | 4 | 6138 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,2 |  |  | total_charge_capacity | 4 | 6139 |  | Double | 32 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,2 |  |  | total_discharge_capacity | 4 | 6141 |  | Double | 32 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,2 |  |  | rack_accumulated_charge_quantity_for_a_single_time | 4 | 6143 |  | Double | 32 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,2 |  |  | rack_accumulated_discharge_quantity_for_a_single_time | 4 | 6145 |  | Double | 32 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,2 |  |  | allow_charge_capacity | 4 | 6147 |  | Double | 32 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,2 |  |  | allow_discharge_capacity | 4 | 6149 |  | Double | 32 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
array | 1 | rack_list,2 |  |  | module_soc | 4 |  |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 | 6151 | 8 | false
array | 1 | rack_list,2 |  |  | cell_volt | 4 |  |  | Double | 16 | Unsigned | Big Endian | 0.001 | 3 | 0 | false |  | false |  | false | 0 | 6191 | 416 | false
array | 1 | rack_list,2 |  |  | cell_temp | 4 |  |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | -40 | false |  | false |  | false | 0 | 6891 | 416 | false
array | 1 | rack_list,2 |  |  | cell_soc | 4 |  |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 | 7591 | 416 | false
array | 1 | rack_list,2 |  |  | cell_soh | 4 |  |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 | 8291 | 416 | false
array | 1 | rack_list,2 |  |  | cell_terminal_temp | 4 |  |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | -40 | false |  | false |  | false | 1 | 8991 | 100 | false
individual | 1 | rack_list,3 |  |  | rack_state | 4 | 9100 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "初始化" }, { "input": "1", "output": "充電" }, { "input": "2", "output": "放電" }, { "input": "3", "output": "就緒" }, { "input": "4", "output": "群集維護" }, { "input": "5", "output": "禁止充電" }, { "input": "6", "output": "禁止放電" }, { "input": "7", "output": "禁止充放電" }, { "input": "8", "output": "故障" }, { "input": "9", "output": "故障恢復" }, { "input": "10", "output": "測試模式" } ] | false | 1 |  | 1 | false
individual | 1 | rack_list,3 |  |  | allow_charge_max_power | 4 | 9101 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,3 |  |  | allow_discharge_max_power | 4 | 9102 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,3 |  |  | allow_charge_max_volt | 4 | 9103 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,3 |  |  | allow_discharge_max_volt | 4 | 9104 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,3 |  |  | allow_charge_max_current | 4 | 9105 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,3 |  |  | allow_discharge_max_current | 4 | 9106 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,3 |  |  | rack_input_1 | 4 | 9107 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "Off" }, { "input": "1", "output": "On" } ] | false | 1 |  | 1 | false
individual | 1 | rack_list,3 |  |  | rack_input_2 | 4 | 9108 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "Off" }, { "input": "1", "output": "On" } ] | false | 1 |  | 1 | false
individual | 1 | rack_list,3 |  |  | rack_input_3 | 4 | 9109 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "Off" }, { "input": "1", "output": "On" } ] | false | 1 |  | 1 | false
individual | 1 | rack_list,3 |  |  | rack_input_4 | 4 | 9110 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "Off" }, { "input": "1", "output": "On" } ] | false | 1 |  | 1 | false
individual | 1 | rack_list,3 |  |  | rack_input_5 | 4 | 9111 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "Off" }, { "input": "1", "output": "On" } ] | false | 1 |  | 1 | false
individual | 1 | rack_list,3 |  |  | rack_input_6 | 4 | 9112 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "Off" }, { "input": "1", "output": "On" } ] | false | 1 |  | 1 | false
individual | 1 | rack_list,3 |  |  | rack_input_7 | 4 | 9113 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "Off" }, { "input": "1", "output": "On" } ] | false | 1 |  | 1 | false
individual | 1 | rack_list,3 |  |  | rack_input_8 | 4 | 9114 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "Off" }, { "input": "1", "output": "On" } ] | false | 1 |  | 1 | false
individual | 1 | rack_list,3 |  |  | voltage | 4 | 9115 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,3 |  |  | current | 4 | 9116 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | -3200 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,3 |  |  | temperature | 4 | 9117 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | -40 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,3 |  |  | soc | 4 | 9118 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,3 |  |  | soh | 4 | 9119 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,3 |  |  | insulation_resistance | 4 | 9120 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,3 |  |  | cell_avg_voltage | 4 | 9121 |  | Double | 16 | Unsigned | Big Endian | 0.001 | 3 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,3 |  |  | cell_avg_temperature | 4 | 9122 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | -40 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,3 |  |  | max_cell_voltage | 4 | 9123 |  | Double | 16 | Unsigned | Big Endian | 0.001 | 3 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,3 |  |  | max_cell_volt_point_address | 4 | 9124 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,3 |  |  | min_cell_voltage | 4 | 9125 |  | Double | 16 | Unsigned | Big Endian | 0.001 | 3 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,3 |  |  | min_cell_volt_point_address | 4 | 9126 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,3 |  |  | max_cell_temperature | 4 | 9127 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | -40 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,3 |  |  | max_cell_temp_point_address | 4 | 9128 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,3 |  |  | min_cell_temperature | 4 | 9129 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | -40 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,3 |  |  | min_cell_temp_point_address | 4 | 9130 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,3 |  |  | max_cell_soc | 4 | 9131 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,3 |  |  | max_cell_soc_point_address | 4 | 9132 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,3 |  |  | min_cell_soc | 4 | 9133 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,3 |  |  | min_cell_soc_point_address | 4 | 9134 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,3 |  |  | max_cell_soh | 4 | 9135 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,3 |  |  | max_cell_soh_point_address | 4 | 9136 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,3 |  |  | min_cell_soh | 4 | 9137 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,3 |  |  | min_cell_soh_point_address | 4 | 9138 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,3 |  |  | total_charge_capacity | 4 | 9139 |  | Double | 32 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,3 |  |  | total_discharge_capacity | 4 | 9141 |  | Double | 32 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,3 |  |  | rack_accumulated_charge_quantity_for_a_single_time | 4 | 9143 |  | Double | 32 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,3 |  |  | rack_accumulated_discharge_quantity_for_a_single_time | 4 | 9145 |  | Double | 32 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,3 |  |  | allow_charge_capacity | 4 | 9147 |  | Double | 32 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,3 |  |  | allow_discharge_capacity | 4 | 9149 |  | Double | 32 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
array | 1 | rack_list,3 |  |  | module_soc | 4 |  |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 | 9151 | 8 | false
array | 1 | rack_list,3 |  |  | cell_volt | 4 |  |  | Double | 16 | Unsigned | Big Endian | 0.001 | 3 | 0 | false |  | false |  | false | 0 | 9191 | 416 | false
array | 1 | rack_list,3 |  |  | cell_temp | 4 |  |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | -40 | false |  | false |  | false | 0 | 9891 | 416 | false
array | 1 | rack_list,3 |  |  | cell_soc | 4 |  |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 | 10591 | 416 | false
array | 1 | rack_list,3 |  |  | cell_soh | 4 |  |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 | 11291 | 416 | false
array | 1 | rack_list,3 |  |  | cell_terminal_temp | 4 |  |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | -40 | false |  | false |  | false | 1 | 11991 | 100 | false
individual | 1 | rack_list,4 |  |  | rack_state | 4 | 12100 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "初始化" }, { "input": "1", "output": "充電" }, { "input": "2", "output": "放電" }, { "input": "3", "output": "就緒" }, { "input": "4", "output": "群集維護" }, { "input": "5", "output": "禁止充電" }, { "input": "6", "output": "禁止放電" }, { "input": "7", "output": "禁止充放電" }, { "input": "8", "output": "故障" }, { "input": "9", "output": "故障恢復" }, { "input": "10", "output": "測試模式" } ] | false | 1 |  | 1 | false
individual | 1 | rack_list,4 |  |  | allow_charge_max_power | 4 | 12101 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,4 |  |  | allow_discharge_max_power | 4 | 12102 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,4 |  |  | allow_charge_max_volt | 4 | 12103 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,4 |  |  | allow_discharge_max_volt | 4 | 12104 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,4 |  |  | allow_charge_max_current | 4 | 12105 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,4 |  |  | allow_discharge_max_current | 4 | 12106 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,4 |  |  | rack_input_1 | 4 | 12107 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "Off" }, { "input": "1", "output": "On" } ] | false | 1 |  | 1 | false
individual | 1 | rack_list,4 |  |  | rack_input_2 | 4 | 12108 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "Off" }, { "input": "1", "output": "On" } ] | false | 1 |  | 1 | false
individual | 1 | rack_list,4 |  |  | rack_input_3 | 4 | 12109 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "Off" }, { "input": "1", "output": "On" } ] | false | 1 |  | 1 | false
individual | 1 | rack_list,4 |  |  | rack_input_4 | 4 | 12110 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "Off" }, { "input": "1", "output": "On" } ] | false | 1 |  | 1 | false
individual | 1 | rack_list,4 |  |  | rack_input_5 | 4 | 12111 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "Off" }, { "input": "1", "output": "On" } ] | false | 1 |  | 1 | false
individual | 1 | rack_list,4 |  |  | rack_input_6 | 4 | 12112 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "Off" }, { "input": "1", "output": "On" } ] | false | 1 |  | 1 | false
individual | 1 | rack_list,4 |  |  | rack_input_7 | 4 | 12113 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "Off" }, { "input": "1", "output": "On" } ] | false | 1 |  | 1 | false
individual | 1 | rack_list,4 |  |  | rack_input_8 | 4 | 12114 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "Off" }, { "input": "1", "output": "On" } ] | false | 1 |  | 1 | false
individual | 1 | rack_list,4 |  |  | voltage | 4 | 12115 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,4 |  |  | current | 4 | 12116 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | -3200 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,4 |  |  | temperature | 4 | 12117 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | -40 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,4 |  |  | soc | 4 | 12118 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,4 |  |  | soh | 4 | 12119 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,4 |  |  | insulation_resistance | 4 | 12120 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,4 |  |  | cell_avg_voltage | 4 | 12121 |  | Double | 16 | Unsigned | Big Endian | 0.001 | 3 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,4 |  |  | cell_avg_temperature | 4 | 12122 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | -40 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,4 |  |  | max_cell_voltage | 4 | 12123 |  | Double | 16 | Unsigned | Big Endian | 0.001 | 3 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,4 |  |  | max_cell_volt_point_address | 4 | 12124 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,4 |  |  | min_cell_voltage | 4 | 12125 |  | Double | 16 | Unsigned | Big Endian | 0.001 | 3 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,4 |  |  | min_cell_volt_point_address | 4 | 12126 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,4 |  |  | max_cell_temperature | 4 | 12127 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | -40 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,4 |  |  | max_cell_temp_point_address | 4 | 12128 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,4 |  |  | min_cell_temperature | 4 | 12129 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | -40 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,4 |  |  | min_cell_temp_point_address | 4 | 12130 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,4 |  |  | max_cell_soc | 4 | 12131 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,4 |  |  | max_cell_soc_point_address | 4 | 12132 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,4 |  |  | min_cell_soc | 4 | 12133 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,4 |  |  | min_cell_soc_point_address | 4 | 12134 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,4 |  |  | max_cell_soh | 4 | 12135 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,4 |  |  | max_cell_soh_point_address | 4 | 12136 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,4 |  |  | min_cell_soh | 4 | 12137 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,4 |  |  | min_cell_soh_point_address | 4 | 12138 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,4 |  |  | total_charge_capacity | 4 | 12139 |  | Double | 32 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,4 |  |  | total_discharge_capacity | 4 | 12141 |  | Double | 32 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,4 |  |  | rack_accumulated_charge_quantity_for_a_single_time | 4 | 12143 |  | Double | 32 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,4 |  |  | rack_accumulated_discharge_quantity_for_a_single_time | 4 | 12145 |  | Double | 32 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,4 |  |  | allow_charge_capacity | 4 | 12147 |  | Double | 32 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,4 |  |  | allow_discharge_capacity | 4 | 12149 |  | Double | 32 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
array | 1 | rack_list,4 |  |  | module_soc | 4 |  |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 | 12151 | 8 | false
array | 1 | rack_list,4 |  |  | cell_volt | 4 |  |  | Double | 16 | Unsigned | Big Endian | 0.001 | 3 | 0 | false |  | false |  | false | 0 | 12191 | 416 | false
array | 1 | rack_list,4 |  |  | cell_temp | 4 |  |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | -40 | false |  | false |  | false | 0 | 12891 | 416 | false
array | 1 | rack_list,4 |  |  | cell_soc | 4 |  |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 | 13591 | 416 | false
array | 1 | rack_list,4 |  |  | cell_soh | 4 |  |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 | 14291 | 416 | false
array | 1 | rack_list,4 |  |  | cell_terminal_temp | 4 |  |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | -40 | false |  | false |  | false | 1 | 14991 | 100 | false
individual | 1 | rack_list,5 |  |  | rack_state | 4 | 15100 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "初始化" }, { "input": "1", "output": "充電" }, { "input": "2", "output": "放電" }, { "input": "3", "output": "就緒" }, { "input": "4", "output": "群集維護" }, { "input": "5", "output": "禁止充電" }, { "input": "6", "output": "禁止放電" }, { "input": "7", "output": "禁止充放電" }, { "input": "8", "output": "故障" }, { "input": "9", "output": "故障恢復" }, { "input": "10", "output": "測試模式" } ] | false | 1 |  | 1 | false
individual | 1 | rack_list,5 |  |  | allow_charge_max_power | 4 | 15101 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,5 |  |  | allow_discharge_max_power | 4 | 15102 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,5 |  |  | allow_charge_max_volt | 4 | 15103 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,5 |  |  | allow_discharge_max_volt | 4 | 15104 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,5 |  |  | allow_charge_max_current | 4 | 15105 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,5 |  |  | allow_discharge_max_current | 4 | 15106 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,5 |  |  | rack_input_1 | 4 | 15107 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "Off" }, { "input": "1", "output": "On" } ] | false | 1 |  | 1 | false
individual | 1 | rack_list,5 |  |  | rack_input_2 | 4 | 15108 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "Off" }, { "input": "1", "output": "On" } ] | false | 1 |  | 1 | false
individual | 1 | rack_list,5 |  |  | rack_input_3 | 4 | 15109 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "Off" }, { "input": "1", "output": "On" } ] | false | 1 |  | 1 | false
individual | 1 | rack_list,5 |  |  | rack_input_4 | 4 | 15110 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "Off" }, { "input": "1", "output": "On" } ] | false | 1 |  | 1 | false
individual | 1 | rack_list,5 |  |  | rack_input_5 | 4 | 15111 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "Off" }, { "input": "1", "output": "On" } ] | false | 1 |  | 1 | false
individual | 1 | rack_list,5 |  |  | rack_input_6 | 4 | 15112 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "Off" }, { "input": "1", "output": "On" } ] | false | 1 |  | 1 | false
individual | 1 | rack_list,5 |  |  | rack_input_7 | 4 | 15113 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "Off" }, { "input": "1", "output": "On" } ] | false | 1 |  | 1 | false
individual | 1 | rack_list,5 |  |  | rack_input_8 | 4 | 15114 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "Off" }, { "input": "1", "output": "On" } ] | false | 1 |  | 1 | false
individual | 1 | rack_list,5 |  |  | voltage | 4 | 15115 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,5 |  |  | current | 4 | 15116 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | -3200 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,5 |  |  | temperature | 4 | 15117 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | -40 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,5 |  |  | soc | 4 | 15118 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,5 |  |  | soh | 4 | 15119 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,5 |  |  | insulation_resistance | 4 | 15120 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,5 |  |  | cell_avg_voltage | 4 | 15121 |  | Double | 16 | Unsigned | Big Endian | 0.001 | 3 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,5 |  |  | cell_avg_temperature | 4 | 15122 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | -40 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,5 |  |  | max_cell_voltage | 4 | 15123 |  | Double | 16 | Unsigned | Big Endian | 0.001 | 3 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,5 |  |  | max_cell_volt_point_address | 4 | 15124 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,5 |  |  | min_cell_voltage | 4 | 15125 |  | Double | 16 | Unsigned | Big Endian | 0.001 | 3 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,5 |  |  | min_cell_volt_point_address | 4 | 15126 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,5 |  |  | max_cell_temperature | 4 | 15127 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | -40 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,5 |  |  | max_cell_temp_point_address | 4 | 15128 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,5 |  |  | min_cell_temperature | 4 | 15129 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | -40 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,5 |  |  | min_cell_temp_point_address | 4 | 15130 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,5 |  |  | max_cell_soc | 4 | 15131 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,5 |  |  | max_cell_soc_point_address | 4 | 15132 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,5 |  |  | min_cell_soc | 4 | 15133 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,5 |  |  | min_cell_soc_point_address | 4 | 15134 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,5 |  |  | max_cell_soh | 4 | 15135 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,5 |  |  | max_cell_soh_point_address | 4 | 15136 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,5 |  |  | min_cell_soh | 4 | 15137 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,5 |  |  | min_cell_soh_point_address | 4 | 15138 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,5 |  |  | total_charge_capacity | 4 | 15139 |  | Double | 32 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,5 |  |  | total_discharge_capacity | 4 | 15141 |  | Double | 32 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,5 |  |  | rack_accumulated_charge_quantity_for_a_single_time | 4 | 15143 |  | Double | 32 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,5 |  |  | rack_accumulated_discharge_quantity_for_a_single_time | 4 | 15145 |  | Double | 32 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,5 |  |  | allow_charge_capacity | 4 | 15147 |  | Double | 32 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 | rack_list,5 |  |  | allow_discharge_capacity | 4 | 15149 |  | Double | 32 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
array | 1 | rack_list,5 |  |  | module_soc | 4 |  |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 | 15151 | 8 | false
array | 1 | rack_list,5 |  |  | cell_volt | 4 |  |  | Double | 16 | Unsigned | Big Endian | 0.001 | 3 | 0 | false |  | false |  | false | 0 | 15191 | 416 | false
array | 1 | rack_list,5 |  |  | cell_temp | 4 |  |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | -40 | false |  | false |  | false | 0 | 15891 | 416 | false
array | 1 | rack_list,5 |  |  | cell_soc | 4 |  |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 | 16591 | 416 | false
array | 1 | rack_list,5 |  |  | cell_soh | 4 |  |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 | 17291 | 416 | false
array | 1 | rack_list,5 |  |  | cell_terminal_temp | 4 |  |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | -40 | false |  | false |  | false | 0 | 17991 | 100 | false
individual | 1 |  |  |  | tms_status | 4 | 60100 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "Off mode" }, { "input": "1", "output": "Cooling mode" }, { "input": "2", "output": "Heating mode" }, { "input": "3", "output": "Auto cycle mode" } ] | false | 1 |  | 1 | false
individual | 1 |  |  |  | tms_status_code | 4 | 60100 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  |  | k1_relay_status | 4 | 60101 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "Opened" }, { "input": "1", "output": "Closing" } ] | false | 1 |  | 1 | false
individual | 1 |  |  |  | k2_relay_status | 4 | 60102 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "Opened" }, { "input": "1", "output": "Closing" } ] | false | 1 |  | 1 | false
individual | 1 |  |  |  | preheat_mode_feedback | 4 | 60103 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "Exit preheat mode" }, { "input": "1", "output": "Enter preheat mode" } ] | false | 1 |  | 1 | false
individual | 1 |  |  |  | tms_outlet_temp | 4 | 60104 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | -40 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  |  | tms_return_temp | 4 | 60105 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | -40 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  |  | container_temp_a | 4 | 60106 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | -40 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  |  | tms_inlet_pressure | 4 | 60107 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  |  | tms_outlet_pressure | 4 | 60108 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  |  | container_humidity_a | 4 | 60109 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  |  | tms_fault_code | 4 | 60110 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  |  | tms_fault | 4 | 60110 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "正常" }, { "input": "1", "output": "BMS & TMS CAN通訊異常" }, { "input": "2", "output": "HVRL 高壓接觸器黏連" }, { "input": "3", "output": "PTC K2 繼電器故障" }, { "input": "4", "output": "ACDC_A 過壓欠壓故障" }, { "input": "5", "output": "ACDC_A 自身故障" }, { "input": "6", "output": "ACDC_B 過壓欠壓故障" }, { "input": "7", "output": "ACDC_B 自身故障" }, { "input": "8", "output": "Fan 風機故障" }, { "input": "9", "output": "HP 高壓傳感器故障" }, { "input": "10", "output": "HPH 高壓過高" }, { "input": "11", "output": "HPL 高壓過低" }, { "input": "12", "output": "LP 低壓傳感器故障" }, { "input": "13", "output": "LPH 低壓過高" }, { "input": "14", "output": "LPL 低壓過低" }, { "input": "15", "output": "OL 出水溫度傳感器故障'" }, { "input": "16", "output": " IL 進水溫度傳感器故障" }, { "input": "17", "output": "P 水泵故障" }, { "input": "18", "output": "IF 進水水壓傳感器故障" }, { "input": "19", "output": "AT 環境溫濕度傳感器故障" }, { "input": "20", "output": "AC 驅動通訊丟失故障" }, { "input": "21", "output": "AC 壓縮機控制器故障" }, { "input": "22", "output": "PTC 過溫故障" }, { "input": "23", "output": "OF 出水水壓傳感器故障" }, { "input": "24", "output": "PE 進出水壓差過低故障" }, { "input": "25", "output": "PS 高壓壓力開關故障" }, { "input": "26", "output": "CF 壓縮機故障" }, { "input": "27", "output": "PTC 故障" }, { "input": "28", "output": "PE 進出水壓差過高故障" }, { "input": "29", "output": "LIP3 進水壓力過低故障" }, { "input": "30", "output": "HI3 進水溫度過高警報" }, { "input": "31", "output": "LI3 進水溫度過低警報" }, { "input": "32", "output": "HO3 出水溫度過高警報" }, { "input": "33", "output": "LO3 出水溫度過低警報" }, { "input": "34", "output": "ST2 吸氣溫度傳感器故障" }, { "input": "35", "output": "EET3 排氣傳感器故障" }, { "input": "36", "output": "HET3 排氣溫度過高警報" }, { "input": "37", "output": "EXX 相序警報" }, { "input": "38", "output": "EBT3 板換傳感器故障" }, { "input": "39", "output": "HET3 板換溫度過低警報" }, { "input": "40", "output": "水泵進口壓力低警報" }, { "input": "41", "output": "水泵進口壓力超低警報" } ] | false | 0 |  | 1 | false
individual | 1 |  |  |  | tms_fault_level | 4 | 60111 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | acdc_a_voltage | 4 | 60112 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  |  | water_pump_pwm | 4 | 60113 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  |  | hv_value | 4 | 60114 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  |  | lv_value | 4 | 60115 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  |  | fan_pwm | 4 | 60116 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  |  | electronic_expansion_valve_opening | 4 | 60117 |  | Int | 16 | Unsigned | Big Endian | 2.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  |  | compressor_voltage | 4 | 60118 |  | Int | 16 | Unsigned | Big Endian | 3.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  |  | compressor_speed | 4 | 60119 |  | Int | 16 | Unsigned | Big Endian | 100.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  |  | ptc_temperature_switch_status | 4 | 60120 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "Opened" }, { "input": "1", "output": "Closing" } ] | false | 1 |  | 1 | false
individual | 1 |  |  |  | dehumidification_status | 4 | 60121 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "Opened" }, { "input": "1", "output": "Closing" } ] | false | 1 |  | 1 | false
individual | 1 |  | TMS_AC_ERROR | 液冷AC故障 | ac_fault | 4 | 60122 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "No fault" } ] | false | 1 |  | 1 | false
individual | 1 |  |  |  | apparent_power | 4 | 60127 |  | Int | 16 | Unsigned | Big Endian | 10 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  |  | freq | 4 | 60135 |  | Double | 16 | Unsigned | Big Endian | 0.01 | 2 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  |  | active_power | 4 | 60139 |  | Int | 16 | Unsigned | Big Endian | 10 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  |  | reactive_power | 4 | 60140 |  | Int | 16 | Unsigned | Big Endian | 10 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  |  | ups_status_code | 4 | 60144 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  |  | ups_status | 4 | 60144 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "1", "output": "打開" }, { "input": "2", "output": "關閉" }, { "input": "3", "output": "開機" }, { "input": "4", "output": "待機" }, { "input": "7", "output": "關閉失敗" }, { "input": "8", "output": "打開失敗" } ] | false | 1 |  | 1 | false
individual | 1 |  |  |  | ups_soc | 4 | 60147 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  | AUXI_POWER_ABNORMALITY | UPS_輔電異常 | auxi_power_abnormality | 4 | 60149 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 |  | CIRCUIT_BREAKER_FEEDBACK | 輔電斷路器異常 | circuit_breaker_feedback | 4 | 60150 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 |  | CONTAINER_ACCESS_CTRL | 門禁開啟 | container_access_ctrl | 4 | 60151 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 |  | PCS_EMRG_STOP | PCS急停 | pcs_epo | 4 | 60152 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 |  | SPD_FEEDBACK_2 | SPD異常 | spd_feedback_2 | 4 | 60153 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 |  | FLOOD | 水位異常 | flood | 4 | 60154 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 |  | COMB_GAS_ALARM | 可燃氣體告警 | comb_gas_alarm | 4 | 60155 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 |  | EXPRF_FAN_ALARM | 排氣風扇開啟 | fan_status | 4 | 60156 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 |  | EXPRF_FAN_ALARM | 排氣風扇故障 | fan_error | 4 | 60157 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 |  | CONTAINER_EMRG_STOP | 急停觸發 | container_epo | 4 | 60158 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 |  | FIRE_PROT_FAULT | 消防故障 | fire_prot_fault | 4 | 60159 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 |  | FIRE_PROT_ALARM_I | 消防煙感/溫感偵測告警 | fire_prot_alarm_i | 4 | 60160 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 1 |  | 1 | false
individual | 1 |  | FIRE_PROT_ALARM_II | 消防2級保護觸發 | fire | 4 | 60161 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | true | 2 |  | 1 | false
individual | 1 |  |  |  | bms_status | 4 | 60166 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "Auto mode" }, { "input": "1", "output": "BMS control mode" } ] | false | 1 |  | 1 | false