## Connection Config
Connection Type | Device Brand | Device Name | Device Type | IP | Port | Timeout | Interval | Destination | Destination Location
TCP | Fimer | PCS_2 | pcs | 192.168.100.103 | 6001 | 3000 | 1000 | filesystem | data

## Modbus Address
address type | unit id | group | code name | display name | address name | function code | address | fix value | data type | bit length | signed type | endianness | scale | decimal places | offset | enable bit configuration | bit configuration | enable parse configuration | parse configuration | is warning variable | warning level | start address | data count | is heartbeat address | heartbeat interval
individual | 1 |  |  |  | heartbeat | 3 | 42240 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | control_word | 3 | 42241 |  | Bit | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | true | { "bit0": { "codeName": "", "displayName": "逆變器操作:", "triggerName": "啟用", "nonTriggerName": "禁用" }, "bit1": { "codeName": "", "displayName": "逆變器併網:", "triggerName": "允許", "nonTriggerName": "不允許" }, "bit2": { "codeName": "", "displayName": "電池連接:", "triggerName": "允許", "nonTriggerName": "不允許" }, "bit3": { "codeName": "", "displayName": "故障重置:", "triggerName": "重置", "nonTriggerName": "無" }, "bit4": { "codeName": "", "displayName": "轉移跳脫:", "triggerName": "作用中", "nonTriggerName": "正常" }, "bit5": { "codeName": "", "displayName": "逆變器重啟:", "triggerName": "重啟", "nonTriggerName": "無" }, "bit6": { "codeName": "", "displayName": "開啟中壓開關:", "triggerName": "開啟", "nonTriggerName": "關閉" }, "bit7": { "codeName": "", "displayName": "關閉中壓開關:", "triggerName": "關閉", "nonTriggerName": "開啟" }, "bit8": { "codeName": "", "displayName": "優先權模式:", "triggerName": "虛功優先", "nonTriggerName": "實功優先" }, "bit9": { "codeName": "", "displayName": "全黑啟動模式:", "triggerName": "啟用", "nonTriggerName": "禁用" }, "bit10": { "codeName": "", "displayName": "CC/CV模式:", "triggerName": "啟用", "nonTriggerName": "禁用" }, "bit11": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit12": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit13": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit14": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit15": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" } } | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | p_ref_operation_mode | 3 | 42242 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | q_ref_operation_mode | 3 | 42243 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | setting_power | 3 | 42244 |  | Int | 16 | Signed | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | setting_reactive_power | 3 | 42245 |  | Int | 16 | Signed | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | setting_active_power_percent | 3 | 42246 |  | Double | 16 | Signed | Big Endian | 0.01 | 2 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | setting_reactive_power_percent | 3 | 42247 |  | Double | 16 | Signed | Big Endian | 0.01 | 2 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | setting_power_factor | 3 | 42248 |  | Double | 16 | Signed | Big Endian | 0.001 | 3 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | vac_reference | 3 | 42249 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | active_power_percent_limit_to_grid | 3 | 42250 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | active_power_percent_limit_from_grid | 3 | 42251 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | reactive_current_positive_percent_limit | 3 | 42252 |  | Double | 16 | Signed | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | reactive_current_negative_percent_limit | 3 | 42253 |  | Double | 16 | Signed | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | user_ac_voltage_ref | 3 | 42254 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | drooping_q_power_offset | 3 | 42255 |  | Double | 16 | Signed | Big Endian | 0.01 | 2 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | user_frequency_ref | 3 | 42256 |  | Double | 16 | Unsigned | Big Endian | 0.01 | 2 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | drooping_power_offset | 3 | 42257 |  | Double | 16 | Signed | Big Endian | 0.01 | 2 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | set_heartbeat | 3 | 42496 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | running_status_code | 3 | 42497 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | running_status | 3 | 42497 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | true | [ { "input": "0", "output": "待機" }, { "input": "1", "output": "靜態補償" }, { "input": "2", "output": "連接電池" }, { "input": "3", "output": "服務模式" }, { "input": "4", "output": "委託模式" }, { "input": "5", "output": "斷開" }, { "input": "6", "output": "斷開中" }, { "input": "7", "output": "連接中" }, { "input": "8", "output": "連接電網" } ] | false | 1 |  | 1 | false
individual | 1 |  |  |  | active_power | 3 | 42498 |  | Int | 16 | Signed | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | reactive_power | 3 | 42499 |  | Int | 16 | Signed | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | volt_avg | 3 | 42500 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | frequency | 3 | 42501 |  | Double | 16 | Unsigned | Big Endian | 0.01 | 2 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | battery_voltage | 3 | 42502 |  | Double | 16 | Signed | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | active_power_limit_to_grid | 3 | 42503 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | active_power_limit_from_grid | 3 | 42504 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | positive_reactive_power_limit | 3 | 42505 |  | Double | 16 | Signed | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | negative_reactive_power_limit | 3 | 42506 |  | Double | 16 | Signed | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | active_fault | 3 | 42545 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | volt_rs | 3 | 42546 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | volt_st | 3 | 42547 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | volt_tr | 3 | 42548 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | current_r | 3 | 42549 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | current_s | 3 | 42550 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | current_t | 3 | 42551 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | dc_active_power | 3 | 42552 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | dc_grounding_current | 3 | 42557 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | dc_isolation_resistance | 3 | 42558 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | ambient_temperature | 3 | 42559 |  | Double | 16 | Signed | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | igbt_temp_m1 | 3 | 42560 |  | Double | 16 | Signed | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | ctrl_section_temp | 3 | 42564 |  | Double | 16 | Signed | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | cabinet_temp_m1 | 3 | 42565 |  | Double | 16 | Signed | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | lcl_section_temp_m1 | 3 | 42569 |  | Double | 16 | Signed | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | humidity | 3 | 42573 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | kwh_energy_charged_to_battery | 3 | 42574 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | mwh_energy_charged_to_battery | 3 | 42575 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | gwh_energy_charged_to_battery | 3 | 42576 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | kwh_energy_discharged_from_battery | 3 | 42577 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | mwh_energy_discharged_from_battery | 3 | 42578 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | gwh_energy_discharged_from_battery | 3 | 42579 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
array | 1 |  |  |  | dc_input_current_m1 | 3 |  |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 | 42582 | 12 | false
individual | 1 |  |  |  | ele_switching | 3 | 42630 |  | Bit | 16 | Signed | Big Endian | 1.0 | 0 | 0 | true | { "bit0": { "codeName": "", "displayName": "AC_M1接觸器:", "triggerName": "開啟", "nonTriggerName": "關閉" }, "bit1": { "codeName": "", "displayName": "AC_M2接觸器:", "triggerName": "開啟", "nonTriggerName": "關閉" }, "bit2": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit3": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit4": { "codeName": "", "displayName": "DC_M1接觸器:", "triggerName": "開啟", "nonTriggerName": "關閉" }, "bit5": { "codeName": "", "displayName": "DC_M2接觸器:", "triggerName": "開啟", "nonTriggerName": "關閉" }, "bit6": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit7": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit8": { "codeName": "", "displayName": "AC_M1斷路器:", "triggerName": "開啟", "nonTriggerName": "關閉" }, "bit9": { "codeName": "", "displayName": "AC_M2斷路器:", "triggerName": "開啟", "nonTriggerName": "關閉" }, "bit10": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit11": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit12": { "codeName": "", "displayName": "DC_M1斷路器:", "triggerName": "開啟", "nonTriggerName": "關閉" }, "bit13": { "codeName": "", "displayName": "DC_M2斷路器:", "triggerName": "開啟", "nonTriggerName": "關閉" }, "bit14": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit15": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" } } | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | ele_switching_2 | 3 | 42631 |  | Bit | 16 | Signed | Big Endian | 1.0 | 0 | 0 | true | { "bit0": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit1": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit2": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit3": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit4": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit5": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit6": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit7": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit8": { "codeName": "", "displayName": "MV斷路器:", "triggerName": "開啟", "nonTriggerName": "關閉" }, "bit9": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit10": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit11": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit12": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit13": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit14": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit15": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" } } | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | inverter_main_status | 3 | 42632 |  | Bit | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | true | { "bit0": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit1": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit2": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit3": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit4": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit5": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit6": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit7": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit8": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit9": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit10": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit11": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit12": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit13": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit14": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit15": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" } } | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | limitation_status_word | 3 | 42633 |  | Bit | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | true | { "bit0": { "codeName": "IGBT_TEMP_LIMITATION", "displayName": "功率受限(IGBT Temp.)", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit1": { "codeName": "P_F_LIMITATION", "displayName": "功率受限(頻率)", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit2": { "codeName": "P_U_LIMITATION", "displayName": "功率受限(電壓)", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit3": { "codeName": "GRID_FAULT_LIMITATION", "displayName": "功率受限(電網故障)", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit4": { "codeName": "EX_POWER_LIMITATION", "displayName": "功率受限(外部功率)", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit5": { "codeName": "FRT_LIMITATION", "displayName": "功率受限(FRT)", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit6": { "codeName": "SHUTDOWN_RAMP_LIMITATION", "displayName": "功率受限(RAMP)", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit7": { "codeName": "GRADIENT_LIMITATION", "displayName": "功率受限(梯度)", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit8": { "codeName": "GRID_ACTIVE_LIMITATION", "displayName": "功率受限(電網活動)", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit9": { "codeName": "AMBIENT_TEMP_LIMITATION", "displayName": "功率受限(環境溫度)", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit10": { "codeName": "CTRL_TEMP_LIMITATION", "displayName": "功率受限(CTRL溫度)", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit11": { "codeName": "AC_DC_TEMP_LIMITATION", "displayName": "功率受限(ACDC溫度)", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit12": { "codeName": "LCL_LIMITATION", "displayName": "功率受限(LCL溫度)", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit13": { "codeName": "BATTERY_VOLT_LIMITATION", "displayName": "功率受限(電池電壓)", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit14": { "codeName": "DC_CURRENT_LIMITATION", "displayName": "功率受限(電池電流)", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit15": { "codeName": "CHARGE_DISCHARGE_LIMITATION", "displayName": "功率受限(充放電電流)", "triggerName": "ON", "nonTriggerName": "OFF" } } | false |  | true | 1 |  | 1 | false
individual | 1 |  |  |  | grid_status | 3 | 42636 |  | Bit | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | true | { "bit0": { "codeName": "", "displayName": "電網欠壓", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit1": { "codeName": "", "displayName": "電網過壓", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit2": { "codeName": "", "displayName": "電網低頻", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit3": { "codeName": "", "displayName": "電網高頻", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit4": { "codeName": "", "displayName": "防孤島已開啟", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit5": { "codeName": "", "displayName": "頻率變化率(RoCoF)跳閘", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit6": { "codeName": "", "displayName": "組合跳脫", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit7": { "codeName": "", "displayName": "移動平均跳脫", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit8": { "codeName": "", "displayName": "零穿越跳脫", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit9": { "codeName": "", "displayName": "低電壓穩態(LVRT)跳脫", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit10": { "codeName": "", "displayName": "高電壓穩態(HVRT)跳脫", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit11": { "codeName": "", "displayName": "外部監控跳脫", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit12": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit13": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit14": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit15": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" } } | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | fan_status | 3 | 42637 |  | Bit | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | true | { "bit0": { "codeName": "", "displayName": "通道1_風扇#1:", "triggerName": "開啟", "nonTriggerName": "關閉" }, "bit1": { "codeName": "", "displayName": "通道1_風扇#2:", "triggerName": "開啟", "nonTriggerName": "關閉" }, "bit2": { "codeName": "", "displayName": "通道1_風扇#3:", "triggerName": "開啟", "nonTriggerName": "關閉" }, "bit3": { "codeName": "", "displayName": "通道1_風扇#4:", "triggerName": "開啟", "nonTriggerName": "關閉" }, "bit4": { "codeName": "", "displayName": "通道2_風扇#1:", "triggerName": "開啟", "nonTriggerName": "關閉" }, "bit5": { "codeName": "", "displayName": "通道2_風扇#2:", "triggerName": "開啟", "nonTriggerName": "關閉" }, "bit6": { "codeName": "", "displayName": "通道2_風扇#3:", "triggerName": "開啟", "nonTriggerName": "關閉" }, "bit7": { "codeName": "", "displayName": "通道2_風扇#4:", "triggerName": "開啟", "nonTriggerName": "關閉" }, "bit8": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit9": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit10": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit11": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit12": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit13": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit14": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit15": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" } } | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | fan_status2 | 3 | 42638 |  | Bit | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | true | { "bit0": { "codeName": "", "displayName": "LCL_M1風扇#1:", "triggerName": "開啟", "nonTriggerName": "關閉" }, "bit1": { "codeName": "", "displayName": "LCL_M1風扇#2:", "triggerName": "開啟", "nonTriggerName": "關閉" }, "bit2": { "codeName": "", "displayName": "LCL_M2風扇#1:", "triggerName": "開啟", "nonTriggerName": "關閉" }, "bit3": { "codeName": "", "displayName": "LCL_M2風扇#2:", "triggerName": "開啟", "nonTriggerName": "關閉" }, "bit4": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit5": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit6": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit7": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit8": { "codeName": "", "displayName": "AC_DC_M1風扇#1:", "triggerName": "開啟", "nonTriggerName": "關閉" }, "bit9": { "codeName": "", "displayName": "AC_DC_M2風扇#2:", "triggerName": "開啟", "nonTriggerName": "關閉" }, "bit10": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit11": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit12": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit13": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit14": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit15": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" } } | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | env_status | 3 | 42639 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | fault_status | 3 | 42640 |  | Bit | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | true | { "bit0": { "codeName": "FAST_POWER_OFF", "displayName": "快速關機(0x6E1C)", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit1": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit2": { "codeName": "RESIDUAL_GROUNDING_CURRENT_FAULT", "displayName": "接地電流突變(0x9105，0x9104)", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit3": { "codeName": "INSULATION_RESISTANCE_FAULT", "displayName": "絕緣阻抗故障(0x9107)", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit4": { "codeName": "GROUNDING_CIRCUIT_OV_FAULT", "displayName": "接地回路過壓（0x9106）", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit5": { "codeName": "REVERSE_CURRENT_FAULT", "displayName": "反向電流故障(0x9108)", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit6": { "codeName": "DC_OC_FAULT", "displayName": "DC過流故障(0x9109)", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit7": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit8": { "codeName": "FAN_FAULT", "displayName": "風扇故障(參閱詳細系統日誌)", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit9": { "codeName": "AC_CONTACTOR_FAULT", "displayName": "交流接觸器故障(0x9121, 0x9120)", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit10": { "codeName": "DC_CONTACTOR_FAULT", "displayName": "直流接觸器故障(0x9125，0x9124)", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit11": { "codeName": "DC_SWITCH_FAULT", "displayName": "直流開關斷開(0x9128)", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit12": { "codeName": "SPD_FAULT", "displayName": "SPD故障(0x9130)", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit13": { "codeName": "DC_INPUT_FUSE_FAULT", "displayName": "直流保險絲故障(0x9153, 0x9131)", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit14": { "codeName": "48V_POWER_SUPPLY_FAULT", "displayName": "48V電源故障(0x9132)", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit15": { "codeName": "MFA_FAULT", "displayName": "內部軟體故障", "triggerName": "ON", "nonTriggerName": "OFF" } } | false |  | true | 2 |  | 1 | false
individual | 1 |  |  |  | fault_status2 | 3 | 42641 |  | Bit | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | true | { "bit0": { "codeName": "48V_BUFFER_FAULT", "displayName": "48V緩衝器故障(0x9133)", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit1": { "codeName": "24V_BUFFER_FAULT", "displayName": "24V緩衝器故障(0x9134)", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit2": { "codeName": "AUX_BREAKER_FAULT", "displayName": "輔電斷路器故障(0x9135)", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit3": { "codeName": "LCL_PRESSURE_SENSOR_FAULT", "displayName": "LCL壓力感測器故障(0x9136)", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit4": { "codeName": "AC_DC_DOOR_FAULT", "displayName": "AC、DC電門故障(0x9137, 0x9138)", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit5": { "codeName": "AC_BREAKER_TRIP", "displayName": "交流斷路器跳閘(0x9140)", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit6": { "codeName": "AC_OC_FAULT", "displayName": "AC過流故障(0x2E00)", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit7": { "codeName": "SHORT_CIRCUIT_FAULT", "displayName": "短路，直流短路故障(0x2E02，0x2E09)", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit8": { "codeName": "BU_CURRENT_DC_FUSE_FAULT", "displayName": "電流差異/直流保險絲熔斷(0x2E05)", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit9": { "codeName": "INPUT_PHASE_LOSS_FAULT", "displayName": "輸入電壓缺相(0x3E00)", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit10": { "codeName": "CTRL_OT_FAULT", "displayName": "CTRL過溫(0x9101)", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit11": { "codeName": "IGBT_OT_FAULT", "displayName": "IGBT過溫(0x9101)", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit12": { "codeName": "AC_DC_OT_FAULT", "displayName": "AC/DC過溫(0x9101)", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit13": { "codeName": "LCL_OT_FAULT", "displayName": "LCL過溫(0x9101)", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit14": { "codeName": "PU_COMM_FAULT", "displayName": "PU通信故障(0x5E07)", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit15": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" } } | false |  | true | 2 |  | 1 | false
individual | 1 |  |  |  | warning_status | 3 | 42642 |  | Bit | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | true | { "bit0": { "codeName": "GROUNDING_CURRENT_WARNING", "displayName": "接地電流突變告警(0xE104)", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit1": { "codeName": "RESIDUAL_CURRENT_WARNING", "displayName": "殘餘電流告警(0xE105)", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit2": { "codeName": "GROUNDING_CIRCUIT_OV_WARNING", "displayName": "接地回路過壓告警(0xE106)", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit3": { "codeName": "INSULATION_RESISTANCE_WARNING", "displayName": "絕緣阻抗低於設定告警(0xE107)", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit4": { "codeName": "TEMP_SENSOR_WARNING", "displayName": "溫度感測器告警", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit5": { "codeName": "SCADA_DATA_WARNING", "displayName": "SCADA數據超出範圍", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit6": { "codeName": "DC_LINK_OV_WARNING", "displayName": "直流連接線過壓告警(0xE130)", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit7": { "codeName": "INPUT_OV_WARNING", "displayName": "輸入過壓告警(0xE131)", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit8": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit9": { "codeName": "CIRCUIT_SPD_WARNING", "displayName": "主電路SPD告警(0xE133)", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit10": { "codeName": "48V_POWER_SUPPLY_WARNING", "displayName": "48V電源告警(0xE135)", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit11": { "codeName": "48V_BUFFER_WARNING", "displayName": "48V緩衝器告警(0xE136)", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit12": { "codeName": "24V_BUFFER_WARNING", "displayName": "24V緩衝器告警(0xE137)", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit13": { "codeName": "AUX_BREAKER_WARNING", "displayName": "輔電斷路器告警(0xE138)", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit14": { "codeName": "LCL_PRESSURE_SENSOR_WARNING", "displayName": "LCL壓力感測器告警(0xE139)", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit15": { "codeName": "AC_DC_DOOR_WARNING", "displayName": "交流/直流電門告警(0xE140，0xE141)", "triggerName": "ON", "nonTriggerName": "OFF" } } | false |  | true | 1 |  | 1 | false
individual | 1 |  |  |  | dc_fuse_m1_status | 3 | 42647 |  | Bit | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | true | { "bit0": { "codeName": "DC_M1_FUSE_1_FAULT", "displayName": "DC_M1保險絲1失效", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit1": { "codeName": "DC_M1_FUSE_2_FAULT", "displayName": "DC_M1保險絲2失效", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit2": { "codeName": "DC_M1_FUSE_3_FAULT", "displayName": "DC_M1保險絲3失效", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit3": { "codeName": "DC_M1_FUSE_4_FAULT", "displayName": "DC_M1保險絲4失效", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit4": { "codeName": "DC_M1_FUSE_5_FAULT", "displayName": "DC_M1保險絲5失效", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit5": { "codeName": "DC_M1_FUSE_6_FAULT", "displayName": "DC_M1保險絲6失效", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit6": { "codeName": "DC_M1_FUSE_7_FAULT", "displayName": "DC_M1保險絲7失效", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit7": { "codeName": "DC_M1_FUSE_8_FAULT", "displayName": "DC_M1保險絲8失效", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit8": { "codeName": "DC_M1_FUSE_9_FAULT", "displayName": "DC_M1保險絲9失效", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit9": { "codeName": "DC_M1_FUSE_10_FAULT", "displayName": "DC_M1保險絲10失效", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit10": { "codeName": "DC_M1_FUSE_11_FAULT", "displayName": "DC_M1保險絲11失效", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit11": { "codeName": "DC_M1_FUSE_12_FAULT", "displayName": "DC_M1保險絲12失效", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit12": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit13": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit14": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit15": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" } } | false |  | true | 2 |  | 1 | false
individual | 1 |  |  |  | dc_fuse_m2_status | 3 | 42648 |  | Bit | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | true | { "bit0": { "codeName": "DC_M2_FUSE_1_FAULT", "displayName": "DC_M2保險絲1失效", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit1": { "codeName": "DC_M2_FUSE_2_FAULT", "displayName": "DC_M2保險絲2失效", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit2": { "codeName": "DC_M2_FUSE_3_FAULT", "displayName": "DC_M2保險絲3失效", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit3": { "codeName": "DC_M2_FUSE_4_FAULT", "displayName": "DC_M2保險絲4失效", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit4": { "codeName": "DC_M2_FUSE_5_FAULT", "displayName": "DC_M2保險絲5失效", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit5": { "codeName": "DC_M2_FUSE_6_FAULT", "displayName": "DC_M2保險絲6失效", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit6": { "codeName": "DC_M2_FUSE_7_FAULT", "displayName": "DC_M2保險絲7失效", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit7": { "codeName": "DC_M2_FUSE_8_FAULT", "displayName": "DC_M2保險絲8失效", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit8": { "codeName": "DC_M2_FUSE_9_FAULT", "displayName": "DC_M2保險絲9失效", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit9": { "codeName": "DC_M2_FUSE_10_FAULT", "displayName": "DC_M2保險絲10失效", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit10": { "codeName": "DC_M2_FUSE_11_FAULT", "displayName": "DC_M2保險絲11失效", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit11": { "codeName": "DC_M2_FUSE_12_FAULT", "displayName": "DC_M2保險絲12失效", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit12": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit13": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit14": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit15": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" } } | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | inverter_inhibits_1 | 3 | 42651 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | inverter_inhibits_2 | 3 | 42652 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | apparent_power | 3 | 42653 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | nominal_grid_voltage | 3 | 42654 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | serial_number | 3 | 42655 |  | Int | 32 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 0 |  | 1 | false
individual | 1 |  |  |  | set_output_heartbeat | 6 | 42240 |  | Bit | 16 | Signed | Big Endian | 1.0 | 0 | 0 | true | { "bit0": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit1": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit2": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit3": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit4": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit5": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit6": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit7": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit8": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit9": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit10": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit11": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit12": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit13": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit14": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" }, "bit15": { "codeName": "", "displayName": "", "triggerName": "ON", "nonTriggerName": "OFF" } } | false |  | false | 0 |  | 1 | true | 1000