## Connection Config
Connection Type | Device Brand | Device Name | Device Type | IP | Port | Timeout | Interval | Destination | Destination Location
TCP | FT-PI01 | UPS | ups | 192.168.100.110 | 502 | 3000 | 1000 | filesystem | data

## Modbus Address
address type | unit id | group | display name | address name | function code | address | fix value | data type | bit length | signed type | endianness | scale | decimal places | offset | enable bit configuration | bit configuration | enable parse configuration | parse configuration | is warning variable | warning level | start address | data count | is heartbeat address | heartbeat interval
individual | 1 |  |  | soc | 4 | 4 |  | Int | 16 | Unsigned | Big Endian | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  | voltage | 4 | 5 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  | temp | 4 | 7 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  | input_freq | 4 | 18 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  | input_voltage | 4 | 21 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  | output_freq | 4 | 50 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  | output_voltage | 4 | 53 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  | output_load | 4 | 65 |  | Double | 16 | Unsigned | Big Endian | 0.1 | 1 | 0 | false |  | false |  | false | 0 |  | 1 | false