## Connection Config
Connection Type | Device Brand | Device Name | Device Type | IP | Port | Timeout | Interval | Destination | Destination Location
TCP | PM335 | METER_MAIN | meter | 192.168.100.103 | 6004 | 3000 | 1000 | filesystem | data

## Modbus Address
address type | unit id | group | display name | address name | function code | address | fix value | data type | bit length | signed type | endianness | scale | decimal places | offset | enable bit configuration | bit configuration | enable parse configuration | parse configuration | is warning variable | warning level | start address | data count | is heartbeat address | heartbeat interval
individual | 1 |  |  | voltage_a | 4 | 13952 |  | Int | 32 | Unsigned | Little Endian Byte Swap | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  | voltage_b | 4 | 13954 |  | Int | 32 | Unsigned | Little Endian Byte Swap | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  | voltage_c | 4 | 13956 |  | Int | 32 | Unsigned | Little Endian Byte Swap | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  | current_a | 4 | 13958 |  | Double | 32 | Unsigned | Little Endian Byte Swap | 0.01 | 2 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  | current_b | 4 | 13960 |  | Double | 32 | Unsigned | Little Endian Byte Swap | 0.01 | 2 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  | current_c | 4 | 13962 |  | Double | 32 | Unsigned | Little Endian Byte Swap | 0.01 | 2 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  | pa | 4 | 13964 |  | Int | 32 | Signed | Little Endian Byte Swap | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  | pb | 4 | 13966 |  | Int | 32 | Signed | Little Endian Byte Swap | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  | pc | 4 | 13968 |  | Int | 32 | Signed | Little Endian Byte Swap | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  | qa | 4 | 13970 |  | Int | 32 | Signed | Little Endian Byte Swap | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  | qb | 4 | 13972 |  | Int | 32 | Signed | Little Endian Byte Swap | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  | qc | 4 | 13974 |  | Int | 32 | Signed | Little Endian Byte Swap | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  | sa | 4 | 13976 |  | Int | 32 | Unsigned | Little Endian Byte Swap | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  | sb | 4 | 13978 |  | Int | 32 | Unsigned | Little Endian Byte Swap | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  | sc | 4 | 13980 |  | Int | 32 | Unsigned | Little Endian Byte Swap | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  | pfa | 4 | 13982 |  | Double | 32 | Signed | Little Endian Byte Swap | 0.001 | 3 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  | pfb | 4 | 13984 |  | Double | 32 | Signed | Little Endian Byte Swap | 0.001 | 3 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  | pfc | 4 | 13986 |  | Double | 32 | Signed | Little Endian Byte Swap | 0.001 | 3 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  | voltage_ab | 4 | 14012 |  | Int | 32 | Unsigned | Little Endian Byte Swap | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  | voltage_bc | 4 | 14014 |  | Int | 32 | Unsigned | Little Endian Byte Swap | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  | voltage_ca | 4 | 14016 |  | Int | 32 | Unsigned | Little Endian Byte Swap | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  | total_active_power | 4 | 14336 |  | Int | 32 | Signed | Little Endian Byte Swap | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  | total_reactive_power | 4 | 14338 |  | Int | 32 | Signed | Little Endian Byte Swap | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  | total_apparent_power | 4 | 14340 |  | Int | 32 | Unsigned | Little Endian Byte Swap | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  | total_power_factor | 4 | 14342 |  | Double | 32 | Signed | Little Endian Byte Swap | 0.001 | 3 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  | line_voltage_avg | 4 | 14356 |  | Int | 32 | Unsigned | Little Endian Byte Swap | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  | voltage_avg | 4 | 14358 |  | Int | 32 | Unsigned | Little Endian Byte Swap | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  | current_avg | 4 | 14360 |  | Double | 32 | Unsigned | Little Endian Byte Swap | 0.01 | 2 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  | in_current | 4 | 14466 |  | Int | 32 | Unsigned | Little Endian Byte Swap | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  | frequency | 4 | 14468 |  | Double | 32 | Unsigned | Little Endian Byte Swap | 0.01 | 2 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  | accu_demand_kw | 4 | 14622 |  | Int | 32 | Unsigned | Little Endian Byte Swap | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  | accu_demand_kvar | 4 | 14624 |  | Int | 32 | Unsigned | Little Endian Byte Swap | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  | accu_demand_kva | 4 | 14626 |  | Int | 32 | Unsigned | Little Endian Byte Swap | 1.0 | 0 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  | ac_energy_imp | 4 | 14720 |  | Double | 32 | Unsigned | Little Endian Byte Swap | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false
individual | 1 |  |  | ac_energy_exp | 4 | 14722 |  | Double | 32 | Unsigned | Little Endian Byte Swap | 0.1 | 1 | 0 | false |  | false |  | false | 1 |  | 1 | false